## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Substation Common |  |  | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Substation Common |  |  | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Substation Common |  |  | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Substation Common |  |  | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Substation Common |  |  | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Substation Common |  |  | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer 1 | 33kV | Transformer | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED1 | 3003
29 | Transformer 1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 16
30 | Transformer 1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 17
31 | Transformer 1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 18
32 | Transformer 1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 19
33 | Transformer 1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 20
34 | Transformer 1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 21
35 | Transformer 1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 22
36 | Transformer 1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 23
37 | Transformer 1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 24
38 | Transformer 1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 25
39 | Transformer 1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 26
40 | Transformer 1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 27
41 | Transformer 1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 28
42 | Transformer 1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 29
43 | Transformer 1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 30
44 | Transformer 1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 31
45 | Transformer 1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 32
46 | Transformer 1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 33
47 | Transformer 1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 34
48 | Transformer 1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 35
49 | Transformer 1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 36
50 | Transformer 1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 37
51 | Transformer 1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
52 | Transformer 1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
53 | Transformer 1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
54 | Transformer 1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
55 | Transformer 1 | 33kV | Transformer | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED1 | 10001
56 | Transformer 1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
57 | Transformer 1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
58 | Transformer 1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
59 | Transformer 1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
60 | Transformer 1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
61 | Transformer 1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
62 | Transformer 1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
63 | Transformer 1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
64 | Transformer 1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
65 | Transformer 1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
66 | Transformer 1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
67 | Transformer 1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
68 | Transformer 1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
69 | Transformer 1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
70 | Transformer 1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
71 | Transformer 1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
72 | Transformer 1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
73 | Transformer -1(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 38
74 | Transformer -1(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 39
75 | Transformer -1(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 40 |  |  |  | AC CMR to be used
76 | Transformer -1(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 41
77 | Transformer -1(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 42
78 | Transformer -1(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 43
79 | Transformer -1(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 44
80 | Transformer -1(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 45
81 | Transformer -1(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
82 | Transformer -1(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
83 | Transformer -1(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
84 | Transformer -1(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
85 | Transformer -1(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
86 | Transformer 2 | 33kV | Transformer | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED1 | 3004
87 | Transformer 2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 46
88 | Transformer 2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 47
89 | Transformer 2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 48
90 | Transformer 2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 49
91 | Transformer 2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 50
92 | Transformer 2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 51
93 | Transformer 2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 52
94 | Transformer 2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 53
95 | Transformer 2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 54
96 | Transformer 2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 55
97 | Transformer 2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 56
98 | Transformer 2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 57
99 | Transformer 2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 58
100 | Transformer 2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 59
101 | Transformer 2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 60
102 | Transformer 2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 61
103 | Transformer 2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 62
104 | Transformer 2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 63
105 | Transformer 2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 64
106 | Transformer 2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 65
107 | Transformer 2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 66
108 | Transformer 2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 67
109 | Transformer 2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
110 | Transformer 2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
111 | Transformer 2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
112 | Transformer 2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
113 | Transformer 2 | 33kV | Transformer | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED1 | 10002
114 | Transformer 2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
115 | Transformer 2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
116 | Transformer 2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
117 | Transformer 2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
118 | Transformer 2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
119 | Transformer 2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
120 | Transformer 2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
121 | Transformer 2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
122 | Transformer 2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
123 | Transformer 2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
124 | Transformer 2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
125 | Transformer 2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
126 | Transformer 2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
127 | Transformer 2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
128 | Transformer 2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
129 | Transformer 2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
130 | Transformer 2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
131 | Transformer -2(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 68
132 | Transformer -2(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 69
133 | Transformer -2(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 70 |  |  |  | AC CMR to be used
134 | Transformer -2(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 71
135 | Transformer -2(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 72
136 | Transformer -2(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 73
137 | Transformer -2(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 74
138 | Transformer -2(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 75
139 | Transformer -2(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
140 | Transformer -2(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
141 | Transformer -2(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
142 | Transformer -2(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
143 | Transformer -2(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
144 | 33kV Incomer 1 | 33kV | Incomer | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3005
145 | 33kV Incomer 1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 76
146 | 33kV Incomer 1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 77
147 | 33kV Incomer 1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 78
148 | 33kV Incomer 1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 79
149 | 33kV Incomer 1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 80
150 | 33kV Incomer 1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 81
151 | 33kV Incomer 1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 82
152 | 33kV Incomer 1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 83
153 | 33kV Incomer 1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 84
154 | 33kV Incomer 1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 85
155 | 33kV Incomer 1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13012
156 | 33kV Incomer 1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13013
157 | 33kV Incomer 1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13014
158 | 33kV Incomer 1 | 33kV | Incomer | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10003
159 | 33kV Incomer 1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5048
160 | 33kV Incomer 1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5049
161 | 33kV Incomer 1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5050
162 | 33kV Incomer 1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5051
163 | 33kV Incomer 1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5052
164 | 33kV Incomer 1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5053
165 | 33kV Incomer 1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5054
166 | 33kV Incomer 1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5055
167 | 33kV Incomer 1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5056
168 | 33kV Incomer 1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5057
169 | 33kV Incomer 1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5058
170 | 33kV Incomer 1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5059
171 | 33kV Incomer 1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5060
172 | 33kV Incomer 1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5061
173 | 33kV Incomer 1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5062
174 | 33kV Incomer 1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
175 | 33kV Incomer 1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
176 | 33kV Incomer 1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5065
177 | 33kV Incomer 1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5066
178 | 33kV Incomer 2 | 33kV | Incomer | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3006
179 | 33kV Incomer 2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 86
180 | 33kV Incomer 2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 87
181 | 33kV Incomer 2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 88
182 | 33kV Incomer 2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 89
183 | 33kV Incomer 2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 90
184 | 33kV Incomer 2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 91
185 | 33kV Incomer 2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 92
186 | 33kV Incomer 2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 93
187 | 33kV Incomer 2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 94
188 | 33kV Incomer 2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 95
189 | 33kV Incomer 2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13015
190 | 33kV Incomer 2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13016
191 | 33kV Incomer 2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13017
192 | 33kV Incomer 2 | 33kV | Incomer | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10004
193 | 33kV Incomer 2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5067
194 | 33kV Incomer 2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5068
195 | 33kV Incomer 2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5069
196 | 33kV Incomer 2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5070
197 | 33kV Incomer 2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5071
198 | 33kV Incomer 2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5072
199 | 33kV Incomer 2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5073
200 | 33kV Incomer 2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5074
201 | 33kV Incomer 2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5075
202 | 33kV Incomer 2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5076
203 | 33kV Incomer 2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5077
204 | 33kV Incomer 2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5078
205 | 33kV Incomer 2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5079
206 | 33kV Incomer 2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5080
207 | 33kV Incomer 2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5081
208 | 33kV Incomer 2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5082
209 | 33kV Incomer 2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5083
210 | 33kV Incomer 2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5084
211 | 33kV Incomer 2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5085
212 | Purtiveda | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3007
213 | Purtiveda | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 96
214 | Purtiveda | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 97
215 | Purtiveda | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 98
216 | Purtiveda | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 99
217 | Purtiveda | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 100
218 | Purtiveda | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 101
219 | Purtiveda | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 102
220 | Purtiveda | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 103
221 | Purtiveda | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 104
222 | Purtiveda | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 105
223 | Purtiveda | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 106
224 | Purtiveda | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 107
225 | Purtiveda | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10005
226 | Purtiveda | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
227 | Purtiveda | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13019
228 | Purtiveda | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13020
229 | Purtiveda | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5086
230 | Purtiveda | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5087
231 | Purtiveda | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5088
232 | Purtiveda | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5089
233 | Purtiveda | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5090
234 | Purtiveda | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5091
235 | Purtiveda | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5092
236 | Purtiveda | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5093
237 | Purtiveda | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5094
238 | Purtiveda | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5095
239 | Purtiveda | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5096
240 | Purtiveda | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5097
241 | Purtiveda | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5098
242 | Purtiveda | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5099
243 | Purtiveda | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5100
244 | Purtiveda | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5101
245 | Purtiveda | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5102
246 | Dhalipara | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3008
247 | Dhalipara | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 108
248 | Dhalipara | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 109
249 | Dhalipara | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 110
250 | Dhalipara | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 111
251 | Dhalipara | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 112
252 | Dhalipara | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 113
253 | Dhalipara | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 114
254 | Dhalipara | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 115
255 | Dhalipara | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 116
256 | Dhalipara | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 117
257 | Dhalipara | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 118
258 | Dhalipara | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 119
259 | Dhalipara | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10006
260 | Dhalipara | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
261 | Dhalipara | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13022
262 | Dhalipara | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13023
263 | Dhalipara | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5103
264 | Dhalipara | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5104
265 | Dhalipara | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5105
266 | Dhalipara | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5106
267 | Dhalipara | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5107
268 | Dhalipara | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5108
269 | Dhalipara | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5109
270 | Dhalipara | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5110
271 | Dhalipara | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5111
272 | Dhalipara | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5112
273 | Dhalipara | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5113
274 | Dhalipara | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5114
275 | Dhalipara | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5115
276 | Dhalipara | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5116
277 | Dhalipara | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5117
278 | Dhalipara | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5118
279 | Dhalipara | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5119
280 | Thakdari | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3009
281 | Thakdari | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 120
282 | Thakdari | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 121
283 | Thakdari | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 122
284 | Thakdari | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 123
285 | Thakdari | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 124
286 | Thakdari | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 125
287 | Thakdari | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 126
288 | Thakdari | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 127
289 | Thakdari | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 128
290 | Thakdari | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 129
291 | Thakdari | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 130
292 | Thakdari | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 131
293 | Thakdari | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10007
294 | Thakdari | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
295 | Thakdari | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13025
296 | Thakdari | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13026
297 | Thakdari | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5120
298 | Thakdari | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5121
299 | Thakdari | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5122
300 | Thakdari | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5123
301 | Thakdari | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5124
302 | Thakdari | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5125
303 | Thakdari | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5126
304 | Thakdari | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5127
305 | Thakdari | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5128
306 | Thakdari | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5129
307 | Thakdari | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5130
308 | Thakdari | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5131
309 | Thakdari | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5132
310 | Thakdari | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5133
311 | Thakdari | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5134
312 | Thakdari | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5135
313 | Thakdari | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5136
314 | one 10 DSS1 | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3010
315 | one 10 DSS1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 132
316 | one 10 DSS1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 133
317 | one 10 DSS1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 134
318 | one 10 DSS1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 135
319 | one 10 DSS1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 136
320 | one 10 DSS1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 137
321 | one 10 DSS1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 138
322 | one 10 DSS1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 139
323 | one 10 DSS1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 140
324 | one 10 DSS1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 141
325 | one 10 DSS1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 142
326 | one 10 DSS1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 143
327 | one 10 DSS1 | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10008
328 | one 10 DSS1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
329 | one 10 DSS1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13028
330 | one 10 DSS1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13029
331 | one 10 DSS1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5137
332 | one 10 DSS1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5138
333 | one 10 DSS1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5139
334 | one 10 DSS1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5140
335 | one 10 DSS1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5141
336 | one 10 DSS1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5142
337 | one 10 DSS1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5143
338 | one 10 DSS1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5144
339 | one 10 DSS1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5145
340 | one 10 DSS1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5146
341 | one 10 DSS1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5147
342 | one 10 DSS1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5148
343 | one 10 DSS1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5149
344 | one 10 DSS1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5150
345 | one 10 DSS1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5151
346 | one 10 DSS1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5152
347 | one 10 DSS1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5153
348 | one 10 DSS2 | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3011
349 | one 10 DSS2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 144
350 | one 10 DSS2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 145
351 | one 10 DSS2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 146
352 | one 10 DSS2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 147
353 | one 10 DSS2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 148
354 | one 10 DSS2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 149
355 | one 10 DSS2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 150
356 | one 10 DSS2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 151
357 | one 10 DSS2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 152
358 | one 10 DSS2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 153
359 | one 10 DSS2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 154
360 | one 10 DSS2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 155
361 | one 10 DSS2 | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10009
362 | one 10 DSS2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
363 | one 10 DSS2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
364 | one 10 DSS2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13032
365 | one 10 DSS2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5154
366 | one 10 DSS2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5155
367 | one 10 DSS2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5156
368 | one 10 DSS2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5157
369 | one 10 DSS2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5158
370 | one 10 DSS2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5159
371 | one 10 DSS2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5160
372 | one 10 DSS2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5161
373 | one 10 DSS2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5162
374 | one 10 DSS2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5163
375 | one 10 DSS2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5164
376 | one 10 DSS2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5165
377 | one 10 DSS2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5166
378 | one 10 DSS2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5167
379 | one 10 DSS2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5168
380 | one 10 DSS2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5169
381 | one 10 DSS2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5170
382 | 11kV Incomer 1 | 11kV | Incomer | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3012
383 | 11kV Incomer 1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 156
384 | 11kV Incomer 1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 157
385 | 11kV Incomer 1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 158
386 | 11kV Incomer 1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 159
387 | 11kV Incomer 1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 160
388 | 11kV Incomer 1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 161
389 | 11kV Incomer 1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 162
390 | 11kV Incomer 1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 163
391 | 11kV Incomer 1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 164
392 | 11kV Incomer 1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 165
393 | 11kV Incomer 1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 166
394 | 11kV Incomer 1 | 11kV | Incomer | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10010
395 | 11kV Incomer 1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
396 | 11kV Incomer 1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13034
397 | 11kV Incomer 1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13035
398 | 11kV Incomer 1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5171
399 | 11kV Incomer 1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5172
400 | 11kV Incomer 1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5173
401 | 11kV Incomer 1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5174
402 | 11kV Incomer 1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5175
403 | 11kV Incomer 1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5176
404 | 11kV Incomer 1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5177
405 | 11kV Incomer 1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5178
406 | 11kV Incomer 1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5179
407 | 11kV Incomer 1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5180
408 | 11kV Incomer 1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5181
409 | 11kV Incomer 1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5182
410 | 11kV Incomer 1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5183
411 | 11kV Incomer 1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5184
412 | 11kV Incomer 1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5185
413 | 11kV Incomer 1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5186
414 | 11kV Incomer 1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5187
415 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Open/Close Status | DPI |  |  | Hard | CMR | 3013
416 | Bus Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 167
417 | Bus Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 168
418 | Bus Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 169
419 | Bus Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 170
420 | Bus Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 171
421 | Bus Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 172 |  |  |  | AC CMR to be used
422 | Bus Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 173
423 | Bus Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 174
424 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Open/Close Command | DPC |  |  | Hard | HDR | 10011
425 | 11kV Incomer 2 | 11kV | Incomer | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3014
426 | 11kV Incomer 2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 175
427 | 11kV Incomer 2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 176
428 | 11kV Incomer 2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 177
429 | 11kV Incomer 2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 178
430 | 11kV Incomer 2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 179
431 | 11kV Incomer 2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 180
432 | 11kV Incomer 2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 181
433 | 11kV Incomer 2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 182
434 | 11kV Incomer 2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 183
435 | 11kV Incomer 2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 184
436 | 11kV Incomer 2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 185
437 | 11kV Incomer 2 | 11kV | Incomer | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10012
438 | 11kV Incomer 2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
439 | 11kV Incomer 2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
440 | 11kV Incomer 2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13038
441 | 11kV Incomer 2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5188
442 | 11kV Incomer 2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5189
443 | 11kV Incomer 2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5190
444 | 11kV Incomer 2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5191
445 | 11kV Incomer 2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5192
446 | 11kV Incomer 2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5193
447 | 11kV Incomer 2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5194
448 | 11kV Incomer 2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5195
449 | 11kV Incomer 2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5196
450 | 11kV Incomer 2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5197
451 | 11kV Incomer 2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5198
452 | 11kV Incomer 2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5199
453 | 11kV Incomer 2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5200
454 | 11kV Incomer 2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5201
455 | 11kV Incomer 2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5202
456 | 11kV Incomer 2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5203
457 | 11kV Incomer 2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5204
458 | one 10 DSS-3 | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3015
459 | one 10 DSS-3 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 186
460 | one 10 DSS-3 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 187
461 | one 10 DSS-3 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 188
462 | one 10 DSS-3 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 189
463 | one 10 DSS-3 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 190
464 | one 10 DSS-3 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 191
465 | one 10 DSS-3 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 192
466 | one 10 DSS-3 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 193
467 | one 10 DSS-3 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 194
468 | one 10 DSS-3 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 195
469 | one 10 DSS-3 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 196
470 | one 10 DSS-3 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 197
471 | one 10 DSS-3 | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10013
472 | one 10 DSS-3 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
473 | one 10 DSS-3 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
474 | one 10 DSS-3 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
475 | one 10 DSS-3 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5205
476 | one 10 DSS-3 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5206
477 | one 10 DSS-3 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5207
478 | one 10 DSS-3 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5208
479 | one 10 DSS-3 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5209
480 | one 10 DSS-3 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5210
481 | one 10 DSS-3 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5211
482 | one 10 DSS-3 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5212
483 | one 10 DSS-3 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5213
484 | one 10 DSS-3 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5214
485 | one 10 DSS-3 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5215
486 | one 10 DSS-3 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5216
487 | one 10 DSS-3 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5217
488 | one 10 DSS-3 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5218
489 | one 10 DSS-3 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5219
490 | one 10 DSS-3 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5220
491 | one 10 DSS-3 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5221
492 | one 10 DSS-4 | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3016
493 | one 10 DSS-4 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 198
494 | one 10 DSS-4 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 199
495 | one 10 DSS-4 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 200
496 | one 10 DSS-4 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 201
497 | one 10 DSS-4 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 202
498 | one 10 DSS-4 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 203
499 | one 10 DSS-4 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 204
500 | one 10 DSS-4 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 205
501 | one 10 DSS-4 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 206
502 | one 10 DSS-4 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 207
503 | one 10 DSS-4 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 208
504 | one 10 DSS-4 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 209
505 | one 10 DSS-4 | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10014
506 | one 10 DSS-4 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
507 | one 10 DSS-4 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
508 | one 10 DSS-4 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
509 | one 10 DSS-4 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5222
510 | one 10 DSS-4 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5223
511 | one 10 DSS-4 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5224
512 | one 10 DSS-4 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5225
513 | one 10 DSS-4 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5226
514 | one 10 DSS-4 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5227
515 | one 10 DSS-4 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5228
516 | one 10 DSS-4 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5229
517 | one 10 DSS-4 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5230
518 | one 10 DSS-4 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5231
519 | one 10 DSS-4 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5232
520 | one 10 DSS-4 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5233
521 | one 10 DSS-4 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5234
522 | one 10 DSS-4 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5235
523 | one 10 DSS-4 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5236
524 | one 10 DSS-4 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5237
525 | one 10 DSS-4 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5238
526 | Spare | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3017
527 | Spare | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 210
528 | Spare | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 211
529 | Spare | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 212
530 | Spare | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 213
531 | Spare | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 214
532 | Spare | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 215
533 | Spare | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 216
534 | Spare | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 217
535 | Spare | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 218
536 | Spare | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 219
537 | Spare | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 220
538 | Spare | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 221
539 | Spare | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10015
540 | Spare | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
541 | Spare | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
542 | Spare | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
543 | Spare | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5239
544 | Spare | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5240
545 | Spare | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5241
546 | Spare | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5242
547 | Spare | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5243
548 | Spare | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5244
549 | Spare | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5245
550 | Spare | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5246
551 | Spare | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5247
552 | Spare | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5248
553 | Spare | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5249
554 | Spare | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5250
555 | Spare | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5251
556 | Spare | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5252
557 | Spare | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5253
558 | Spare | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5254
559 | Spare | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5255
560 | Outgoing-8 | 11kV | Outgoing | Circuit Breaker Open/Close Status | DPI |  |  | Soft | IED | 3018
561 | Outgoing-8 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 222
562 | Outgoing-8 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 223
563 | Outgoing-8 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 224
564 | Outgoing-8 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 225
565 | Outgoing-8 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 226
566 | Outgoing-8 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 227
567 | Outgoing-8 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 228
568 | Outgoing-8 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 229
569 | Outgoing-8 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 230
570 | Outgoing-8 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 231
571 | Outgoing-8 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 232
572 | Outgoing-8 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 233
573 | Outgoing-8 | 11kV | Outgoing | Circuit breaker Open/Close Command | DPC |  |  | Soft | IED | 10016
574 | Outgoing-8 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
575 | Outgoing-8 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
576 | Outgoing-8 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
577 | Outgoing-8 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5256
578 | Outgoing-8 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5257
579 | Outgoing-8 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5258
580 | Outgoing-8 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5259
581 | Outgoing-8 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5260
582 | Outgoing-8 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5261
583 | Outgoing-8 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5262
584 | Outgoing-8 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5263
585 | Outgoing-8 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5264
586 | Outgoing-8 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5265
587 | Outgoing-8 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5266
588 | Outgoing-8 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5267
589 | Outgoing-8 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5268
590 | Outgoing-8 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5269
591 | Outgoing-8 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5270
592 | Outgoing-8 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5271
593 | Outgoing-8 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5272
594 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5273
595 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5274
596 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5275
597 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5276
598 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5277
599 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5278
600 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5279