## Signal List
SCADA/Advanced Distribution Management System (ADMS)
SL.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Substation Common |  |  | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Substation Common |  |  | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Substation Common |  |  | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Substation Common |  |  | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Substation Common |  |  | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Substation Common |  |  | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer 1 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer 1 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer 1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer 1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer 1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer 1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer 1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer 1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer 1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer 1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer 1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer 1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer 1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer 1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer 1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer 1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer 1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer 1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer 1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer 1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer 1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer 1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer 1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer 1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer 1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer 1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer 1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer 1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer 1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer 1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer 1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer 1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer 1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer 1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer 1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer 1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer 1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer 1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer 1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer 1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer 1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer 1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer 1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer 1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer 1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer 1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer 1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer 1 -RTCC | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer 1 -RTCC | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer 1 -RTCC | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer 1 -RTCC | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer 1 -RTCC | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer 1 -RTCC | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer 1 -RTCC | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer 1 -RTCC | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer 1 -RTCC | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer 1 -RTCC | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer 1 -RTCC | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer 1 -RTCC | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer 1 -RTCC | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer 2 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer 2 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer 2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer 2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer 2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer 2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer 2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer 2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer 2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer 2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer 2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer 2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer 2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer 2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer 2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer 2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer 2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer 2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer 2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer 2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer 2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer 2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer 2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer 2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer 2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer 2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer 2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer 2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer 2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer 2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer 2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer 2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer 2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer 2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer 2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer 2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer 2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer 2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer 2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer 2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer 2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer 2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer 2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer 2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer 2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer 2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer 2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer 2-RTCC | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer 2-RTCC | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer 2-RTCC | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer 2-RTCC | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer 2-RTCC | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer 2-RTCC | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer 2-RTCC | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer 2-RTCC | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer 2-RTCC | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer 2-RTCC | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer 2-RTCC | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer 2-RTCC | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer 2-RTCC | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer 3 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer 3 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer 3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer 3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer 3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer 3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer 3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer 3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer 3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer 3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer 3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer 3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer 3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer 3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer 3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer 3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer 3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer 3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer 3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer 3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer 3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer 3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer 3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer 3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer 3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer 3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer 3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer 3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer 3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer 3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer 3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer 3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer 3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer 3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer 3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer 3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer 3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer 3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer 3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer 3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer 3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer 3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer 3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer 3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer 3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer 3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer 3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer 3-RTCC | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer 3-RTCC | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer 3-RTCC | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer 3-RTCC | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer 3-RTCC | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer 3-RTCC | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer 3-RTCC | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer 3-RTCC | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer 3-RTCC | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer 3-RTCC | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer 3-RTCC | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer 3-RTCC | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer 3-RTCC | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 112
209 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 113
210 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 114
211 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 115
212 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 116
213 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 117
214 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 118
215 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 119
216 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 120
217 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 121
218 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 122
219 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 123
220 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
221 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13019
222 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13020
223 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10004
224 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10004
225 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5068
226 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5069
227 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5070
228 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5071
229 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5072
230 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5073
231 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5074
232 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5075
233 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5076
234 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5077
235 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5078
236 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5079
237 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5080
238 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5081
239 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5082
240 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
241 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
242 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5085
243 | Mohispota Bisharpara CKT-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5086
244 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 124
245 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 125
246 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 126
247 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 127
248 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 128
249 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 129
250 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 130
251 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 131
252 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 132
253 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 133
254 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 134
255 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 135
256 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
257 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13022
258 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13023
259 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
260 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
261 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5087
262 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5088
263 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5089
264 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5090
265 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5091
266 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5092
267 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5093
268 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5094
269 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5095
270 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5096
271 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5097
272 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5098
273 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5099
274 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5100
275 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5101
276 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5102
277 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5103
278 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5104
279 | Mohispota Bisharpara CKT-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5105
280 | incomer -3 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 136
281 | incomer -3 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 137
282 | incomer -3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 138
283 | incomer -3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 139
284 | incomer -3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 140
285 | incomer -3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 141
286 | incomer -3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 142
287 | incomer -3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 143
288 | incomer -3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 144
289 | incomer -3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 145
290 | incomer -3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 146
291 | incomer -3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 147
292 | incomer -3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 148
293 | incomer -3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
294 | incomer -3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
295 | incomer -3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
296 | incomer -3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
297 | incomer -3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13026
298 | incomer -3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5106
299 | incomer -3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5107
300 | incomer -3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5108
301 | incomer -3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5109
302 | incomer -3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5110
303 | incomer -3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5111
304 | incomer -3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5112
305 | incomer -3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5113
306 | incomer -3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5114
307 | incomer -3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5115
308 | incomer -3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5116
309 | incomer -3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5117
310 | incomer -3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5118
311 | incomer -3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5119
312 | incomer -3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5120
313 | incomer -3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5121
314 | incomer -3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5122
315 | Mandipara | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 149
316 | Mandipara | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 150
317 | Mandipara | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 151
318 | Mandipara | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 152
319 | Mandipara | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 153
320 | Mandipara | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 154
321 | Mandipara | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 155
322 | Mandipara | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 156
323 | Mandipara | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 157
324 | Mandipara | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 158
325 | Mandipara | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 159
326 | Mandipara | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 160
327 | Mandipara | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 161
328 | Mandipara | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 162
329 | Mandipara | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
330 | Mandipara | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
331 | Mandipara | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
332 | Mandipara | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13028
333 | Mandipara | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13029
334 | Mandipara | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5123
335 | Mandipara | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5124
336 | Mandipara | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5125
337 | Mandipara | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5126
338 | Mandipara | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5127
339 | Mandipara | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5128
340 | Mandipara | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5129
341 | Mandipara | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5130
342 | Mandipara | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5131
343 | Mandipara | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5132
344 | Mandipara | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5133
345 | Mandipara | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5134
346 | Mandipara | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5135
347 | Mandipara | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5136
348 | Mandipara | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5137
349 | Mandipara | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5138
350 | Mandipara | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5139
351 | Spare | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 163
352 | Spare | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 164
353 | Spare | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 165
354 | Spare | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 166
355 | Spare | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 167
356 | Spare | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 168
357 | Spare | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 169
358 | Spare | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 170
359 | Spare | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 171
360 | Spare | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 172
361 | Spare | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 173
362 | Spare | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 174
363 | Spare | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 175
364 | Spare | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 176
365 | Spare | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
366 | Spare | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
367 | Spare | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
368 | Spare | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
369 | Spare | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13032
370 | Spare | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5140
371 | Spare | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5141
372 | Spare | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5142
373 | Spare | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5143
374 | Spare | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5144
375 | Spare | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5145
376 | Spare | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5146
377 | Spare | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5147
378 | Spare | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5148
379 | Spare | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5149
380 | Spare | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5150
381 | Spare | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5151
382 | Spare | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5152
383 | Spare | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5153
384 | Spare | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5154
385 | Spare | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5155
386 | Spare | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5156
387 | JRD-III | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 177
388 | JRD-III | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 178
389 | JRD-III | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 179
390 | JRD-III | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 180
391 | JRD-III | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 181
392 | JRD-III | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 182
393 | JRD-III | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 183
394 | JRD-III | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 184
395 | JRD-III | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 185
396 | JRD-III | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 186
397 | JRD-III | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 187
398 | JRD-III | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 188
399 | JRD-III | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 189
400 | JRD-III | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 190
401 | JRD-III | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
402 | JRD-III | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
403 | JRD-III | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
404 | JRD-III | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
405 | JRD-III | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13035
406 | JRD-III | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5157
407 | JRD-III | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5158
408 | JRD-III | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5159
409 | JRD-III | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5160
410 | JRD-III | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5161
411 | JRD-III | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5162
412 | JRD-III | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5163
413 | JRD-III | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5164
414 | JRD-III | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5165
415 | JRD-III | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5166
416 | JRD-III | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5167
417 | JRD-III | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5168
418 | JRD-III | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5169
419 | JRD-III | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5170
420 | JRD-III | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5171
421 | JRD-III | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5172
422 | JRD-III | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5173
423 | Bus-Coupler | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 191
424 | Bus-Coupler | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 192
425 | Bus-Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 193
426 | Bus-Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 194
427 | Bus-Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 195
428 | Bus-Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 196
429 | Bus-Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 197
430 | Bus-Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 198 |  |  |  | AC CMR to be used
431 | Bus-Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 199
432 | Bus-Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 200
433 | Bus-Coupler | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10010
434 | Bus-Coupler | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10010
435 | Incoming - 1 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 201
436 | Incoming - 1 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 202
437 | Incoming - 1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 203
438 | Incoming - 1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 204
439 | Incoming - 1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 205
440 | Incoming - 1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 206
441 | Incoming - 1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 207
442 | Incoming - 1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 208
443 | Incoming - 1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 209
444 | Incoming - 1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 210
445 | Incoming - 1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 211
446 | Incoming - 1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 212
447 | Incoming - 1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 213
448 | Incoming - 1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
449 | Incoming - 1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
450 | Incoming - 1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
451 | Incoming - 1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
452 | Incoming - 1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13038
453 | Incoming - 1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5174
454 | Incoming - 1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5175
455 | Incoming - 1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5176
456 | Incoming - 1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5177
457 | Incoming - 1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5178
458 | Incoming - 1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5179
459 | Incoming - 1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5180
460 | Incoming - 1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5181
461 | Incoming - 1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5182
462 | Incoming - 1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5183
463 | Incoming - 1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5184
464 | Incoming - 1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5185
465 | Incoming - 1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5186
466 | Incoming - 1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5187
467 | Incoming - 1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5188
468 | Incoming - 1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5189
469 | Incoming - 1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5190
470 | Birati | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 214
471 | Birati | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 215
472 | Birati | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 216
473 | Birati | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 217
474 | Birati | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 218
475 | Birati | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 219
476 | Birati | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 220
477 | Birati | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 221
478 | Birati | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 222
479 | Birati | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 223
480 | Birati | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 224
481 | Birati | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 225
482 | Birati | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 226
483 | Birati | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 227
484 | Birati | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
485 | Birati | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
486 | Birati | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
487 | Birati | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
488 | Birati | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
489 | Birati | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5191
490 | Birati | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5192
491 | Birati | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5193
492 | Birati | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5194
493 | Birati | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5195
494 | Birati | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5196
495 | Birati | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5197
496 | Birati | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5198
497 | Birati | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5199
498 | Birati | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5200
499 | Birati | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5201
500 | Birati | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5202
501 | Birati | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5203
502 | Birati | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5204
503 | Birati | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5205
504 | Birati | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5206
505 | Birati | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5207
506 | Jessore Road - 2 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 228
507 | Jessore Road - 2 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 229
508 | Jessore Road - 2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 230
509 | Jessore Road - 2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 231
510 | Jessore Road - 2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 232
511 | Jessore Road - 2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 233
512 | Jessore Road - 2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 234
513 | Jessore Road - 2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 235
514 | Jessore Road - 2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 236
515 | Jessore Road - 2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 237
516 | Jessore Road - 2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 238
517 | Jessore Road - 2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 239
518 | Jessore Road - 2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 240
519 | Jessore Road - 2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 241
520 | Jessore Road - 2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
521 | Jessore Road - 2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
522 | Jessore Road - 2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
523 | Jessore Road - 2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
524 | Jessore Road - 2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
525 | Jessore Road - 2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5208
526 | Jessore Road - 2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5209
527 | Jessore Road - 2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5210
528 | Jessore Road - 2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5211
529 | Jessore Road - 2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5212
530 | Jessore Road - 2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5213
531 | Jessore Road - 2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5214
532 | Jessore Road - 2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5215
533 | Jessore Road - 2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5216
534 | Jessore Road - 2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5217
535 | Jessore Road - 2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5218
536 | Jessore Road - 2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5219
537 | Jessore Road - 2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5220
538 | Jessore Road - 2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5221
539 | Jessore Road - 2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5222
540 | Jessore Road - 2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5223
541 | Jessore Road - 2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5224
542 | New Barrackpore | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 242
543 | New Barrackpore | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 243
544 | New Barrackpore | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 244
545 | New Barrackpore | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 245
546 | New Barrackpore | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 246
547 | New Barrackpore | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 247
548 | New Barrackpore | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 248
549 | New Barrackpore | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 249
550 | New Barrackpore | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 250
551 | New Barrackpore | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 251
552 | New Barrackpore | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 252
553 | New Barrackpore | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 253
554 | New Barrackpore | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 254
555 | New Barrackpore | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 255
556 | New Barrackpore | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
557 | New Barrackpore | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
558 | New Barrackpore | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
559 | New Barrackpore | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
560 | New Barrackpore | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
561 | New Barrackpore | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5225
562 | New Barrackpore | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5226
563 | New Barrackpore | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5227
564 | New Barrackpore | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5228
565 | New Barrackpore | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5229
566 | New Barrackpore | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5230
567 | New Barrackpore | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5231
568 | New Barrackpore | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5232
569 | New Barrackpore | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5233
570 | New Barrackpore | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5234
571 | New Barrackpore | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5235
572 | New Barrackpore | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5236
573 | New Barrackpore | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5237
574 | New Barrackpore | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5238
575 | New Barrackpore | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5239
576 | New Barrackpore | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5240
577 | New Barrackpore | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5241
578 | Bus Coupler - 2 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 256
579 | Bus Coupler - 2 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 257
580 | Bus Coupler - 2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 258
581 | Bus Coupler - 2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 259
582 | Bus Coupler - 2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 260
583 | Bus Coupler - 2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 261
584 | Bus Coupler - 2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 262
585 | Bus Coupler - 2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 263 |  |  |  | AC CMR to be used
586 | Bus Coupler - 2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 264
587 | Bus Coupler - 2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 265
588 | Bus Coupler - 2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10015
589 | Bus Coupler - 2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10015
590 | Jessore Road- 1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 266
591 | Jessore Road- 1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 267
592 | Jessore Road- 1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 268
593 | Jessore Road- 1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 269
594 | Jessore Road- 1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 270
595 | Jessore Road- 1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 271
596 | Jessore Road- 1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 272
597 | Jessore Road- 1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 273
598 | Jessore Road- 1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 274
599 | Jessore Road- 1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 275
600 | Jessore Road- 1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 276
601 | Jessore Road- 1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 277
602 | Jessore Road- 1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 278
603 | Jessore Road- 1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 279
604 | Jessore Road- 1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
605 | Jessore Road- 1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
606 | Jessore Road- 1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
607 | Jessore Road- 1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
608 | Jessore Road- 1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
609 | Jessore Road- 1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5242
610 | Jessore Road- 1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5243
611 | Jessore Road- 1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5244
612 | Jessore Road- 1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5245
613 | Jessore Road- 1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5246
614 | Jessore Road- 1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5247
615 | Jessore Road- 1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5248
616 | Jessore Road- 1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5249
617 | Jessore Road- 1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5250
618 | Jessore Road- 1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5251
619 | Jessore Road- 1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5252
620 | Jessore Road- 1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5253
621 | Jessore Road- 1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5254
622 | Jessore Road- 1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5255
623 | Jessore Road- 1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5256
624 | Jessore Road- 1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5257
625 | Jessore Road- 1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5258
626 | Bisharpara | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 280
627 | Bisharpara | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 281
628 | Bisharpara | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 282
629 | Bisharpara | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 283
630 | Bisharpara | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 284
631 | Bisharpara | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 285
632 | Bisharpara | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 286
633 | Bisharpara | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 287
634 | Bisharpara | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 288
635 | Bisharpara | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 289
636 | Bisharpara | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 290
637 | Bisharpara | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 291
638 | Bisharpara | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 292
639 | Bisharpara | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 293
640 | Bisharpara | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
641 | Bisharpara | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
642 | Bisharpara | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
643 | Bisharpara | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
644 | Bisharpara | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
645 | Bisharpara | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5259
646 | Bisharpara | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5260
647 | Bisharpara | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5261
648 | Bisharpara | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5262
649 | Bisharpara | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5263
650 | Bisharpara | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5264
651 | Bisharpara | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5265
652 | Bisharpara | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5266
653 | Bisharpara | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5267
654 | Bisharpara | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5268
655 | Bisharpara | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5269
656 | Bisharpara | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5270
657 | Bisharpara | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5271
658 | Bisharpara | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5272
659 | Bisharpara | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5273
660 | Bisharpara | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5274
661 | Bisharpara | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5275
662 | Incomer 2 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 294
663 | Incomer 2 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 295
664 | Incomer 2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 296
665 | Incomer 2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 297
666 | Incomer 2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 298
667 | Incomer 2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 299
668 | Incomer 2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 300
669 | Incomer 2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 301
670 | Incomer 2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 302
671 | Incomer 2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 303
672 | Incomer 2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 304
673 | Incomer 2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 305
674 | Incomer 2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 306
675 | Incomer 2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
676 | Incomer 2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
677 | Incomer 2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
678 | Incomer 2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13055
679 | Incomer 2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13056
680 | Incomer 2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5276
681 | Incomer 2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5277
682 | Incomer 2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5278
683 | Incomer 2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5279
684 | Incomer 2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5280
685 | Incomer 2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5281
686 | Incomer 2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5282
687 | Incomer 2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5283
688 | Incomer 2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5284
689 | Incomer 2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5285
690 | Incomer 2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5286
691 | Incomer 2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5287
692 | Incomer 2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5288
693 | Incomer 2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5289
694 | Incomer 2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5290
695 | Incomer 2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5291
696 | Incomer 2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5292
697 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5293
698 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5294
699 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5295
700 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5296
701 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5297
702 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5298
703 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5299