## Signal List
SCADA/Advanced Distribution Management System (ADMS)
SL.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V_DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V_DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V_DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V_DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V_DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Substation common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Substation common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Substation common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Substation common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Substation common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Substation common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5008
29 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5009
30 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5010
31 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5011
32 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5012
33 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5013
34 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5014
35 | Transformer-1 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 16
36 | Transformer-1 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 17
37 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
38 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
39 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
40 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
41 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
42 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
43 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
44 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
45 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
46 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
47 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
48 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
49 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
50 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
51 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
52 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
53 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
54 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
55 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
56 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
57 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
58 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
59 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
60 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
61 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
62 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
63 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
64 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
65 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5025
76 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5026
77 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5027
78 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5028
79 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5029
80 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5030
81 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5031
82 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
84 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
86 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
87 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
88 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
89 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
90 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
91 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
92 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5032
93 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5033
94 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5034
95 | Transformer-2 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 48
96 | Transformer-2 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 49
97 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
98 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
99 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
100 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
101 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
102 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
103 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
104 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
105 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
106 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
107 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
108 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
109 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
110 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
111 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
112 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
113 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
114 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
115 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
116 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
117 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
118 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
119 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
120 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
121 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
122 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
123 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
124 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
125 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5045
136 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5046
137 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5047
138 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5048
139 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5049
140 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5050
141 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5051
142 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
144 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
146 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
147 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
148 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
149 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
150 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
151 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
152 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5052
153 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5053
154 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5054
155 | Transformer-3 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 80
156 | Transformer-3 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 81
157 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
158 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
159 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
160 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
161 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
162 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
163 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
164 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
165 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
166 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
167 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
168 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
169 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
170 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
171 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
172 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
173 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
174 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
175 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
176 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
177 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
178 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
179 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
180 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
181 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
182 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
183 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
184 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
185 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5065
196 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5066
197 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5067
198 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5068
199 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5069
200 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5070
201 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5071
202 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
204 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
206 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
207 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
208 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
209 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
210 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
211 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
212 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5072
213 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5073
214 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5074
215 | Transformer-4 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 112
216 | Transformer-4 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 113
217 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 114
218 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 115
219 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 116
220 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 117
221 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 118
222 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 119
223 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 120
224 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 121
225 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 122
226 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 123
227 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 124
228 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 125
229 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 126
230 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 127
231 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 128
232 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 129
233 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 130
234 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 131
235 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 132
236 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 133
237 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 134
238 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 135
239 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
240 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
241 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
242 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
243 | Transformer-4 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
244 | Transformer-4 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
245 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5075
246 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5076
247 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5077
248 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5078
249 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5079
250 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5080
251 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5081
252 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5082
253 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5083
254 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5084
255 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5085
256 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5086
257 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5087
258 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5088
259 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5089
260 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5090
261 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5091
262 | Transformer-4 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 136
263 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 137
264 | Transformer-4 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 138 |  |  |  | AC CMR to be used
265 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 139
266 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 140
267 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 141
268 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 142
269 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 143
270 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
271 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
272 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5092
273 | Transformer-4 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5093
274 | Transformer-4 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5094
275 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 144
276 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 145
277 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 146
278 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 147
279 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 148
280 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 149
281 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 150
282 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 151
283 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 152
284 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 153
285 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 154
286 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 155
287 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
288 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13025
289 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13026
290 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
291 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
292 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5095
293 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5096
294 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5097
295 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5098
296 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5099
297 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5100
298 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5101
299 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5102
300 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5103
301 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5104
302 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5105
303 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5106
304 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5107
305 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5108
306 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5109
307 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5110
308 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5111
309 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5112
310 | Bagjola-Mondalkanthi-Chandiberia | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5113
311 | SLT/ Chandiberia-2 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 156
312 | SLT/ Chandiberia-2 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 157
313 | SLT/ Chandiberia-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 158
314 | SLT/ Chandiberia-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 159
315 | SLT/ Chandiberia-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 160
316 | SLT/ Chandiberia-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 161
317 | SLT/ Chandiberia-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 162
318 | SLT/ Chandiberia-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 163
319 | SLT/ Chandiberia-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 164
320 | SLT/ Chandiberia-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 165
321 | SLT/ Chandiberia-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 166
322 | SLT/ Chandiberia-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 167
323 | SLT/ Chandiberia-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
324 | SLT/ Chandiberia-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
325 | SLT/ Chandiberia-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13029
326 | SLT/ Chandiberia-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
327 | SLT/ Chandiberia-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
328 | SLT/ Chandiberia-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5114
329 | SLT/ Chandiberia-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5115
330 | SLT/ Chandiberia-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5116
331 | SLT/ Chandiberia-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5117
332 | SLT/ Chandiberia-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5118
333 | SLT/ Chandiberia-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5119
334 | SLT/ Chandiberia-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5120
335 | SLT/ Chandiberia-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5121
336 | SLT/ Chandiberia-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5122
337 | SLT/ Chandiberia-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5123
338 | SLT/ Chandiberia-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5124
339 | SLT/ Chandiberia-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5125
340 | SLT/ Chandiberia-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5126
341 | SLT/ Chandiberia-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5127
342 | SLT/ Chandiberia-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5128
343 | SLT/ Chandiberia-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5129
344 | SLT/ Chandiberia-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5130
345 | SLT/ Chandiberia-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5131
346 | SLT/ Chandiberia-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5132
347 | SLT/ Chandiberia-1 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 168
348 | SLT/ Chandiberia-1 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 169
349 | SLT/ Chandiberia-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 170
350 | SLT/ Chandiberia-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 171
351 | SLT/ Chandiberia-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 172
352 | SLT/ Chandiberia-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 173
353 | SLT/ Chandiberia-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 174
354 | SLT/ Chandiberia-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 175
355 | SLT/ Chandiberia-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 176
356 | SLT/ Chandiberia-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 177
357 | SLT/ Chandiberia-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 178
358 | SLT/ Chandiberia-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 179
359 | SLT/ Chandiberia-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
360 | SLT/ Chandiberia-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13031
361 | SLT/ Chandiberia-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13032
362 | SLT/ Chandiberia-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
363 | SLT/ Chandiberia-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
364 | SLT/ Chandiberia-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5133
365 | SLT/ Chandiberia-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5134
366 | SLT/ Chandiberia-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5135
367 | SLT/ Chandiberia-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5136
368 | SLT/ Chandiberia-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5137
369 | SLT/ Chandiberia-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5138
370 | SLT/ Chandiberia-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5139
371 | SLT/ Chandiberia-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5140
372 | SLT/ Chandiberia-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5141
373 | SLT/ Chandiberia-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5142
374 | SLT/ Chandiberia-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5143
375 | SLT/ Chandiberia-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5144
376 | SLT/ Chandiberia-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5145
377 | SLT/ Chandiberia-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5146
378 | SLT/ Chandiberia-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5147
379 | SLT/ Chandiberia-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5148
380 | SLT/ Chandiberia-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5149
381 | SLT/ Chandiberia-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5150
382 | SLT/ Chandiberia-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5151
383 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 180
384 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 181
385 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 182
386 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 183
387 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 184
388 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 185
389 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 186
390 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 187
391 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 188
392 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 189
393 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 190
394 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 191
395 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
396 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
397 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13035
398 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
399 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
400 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5152
401 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5153
402 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5154
403 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5155
404 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5156
405 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5157
406 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5158
407 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5159
408 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5160
409 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5161
410 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5162
411 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5163
412 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5164
413 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5165
414 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5166
415 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5167
416 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5168
417 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5169
418 | Meenaaurum-Chandiberia CKT | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5170
419 | Spare-1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 192
420 | Spare-1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 193
421 | Spare-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 194
422 | Spare-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 195
423 | Spare-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 196
424 | Spare-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 197
425 | Spare-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 198
426 | Spare-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 199
427 | Spare-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 200
428 | Spare-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 201
429 | Spare-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 202
430 | Spare-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 203
431 | Spare-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 204
432 | Spare-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 205
433 | Spare-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
434 | Spare-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
435 | Spare-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
436 | Spare-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
437 | Spare-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
438 | Spare-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5171
439 | Spare-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5172
440 | Spare-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5173
441 | Spare-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5174
442 | Spare-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5175
443 | Spare-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5176
444 | Spare-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5177
445 | Spare-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5178
446 | Spare-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5179
447 | Spare-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5180
448 | Spare-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5181
449 | Spare-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5182
450 | Spare-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5183
451 | Spare-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5184
452 | Spare-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5185
453 | Spare-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5186
454 | Spare-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5187
455 | Dhankal | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 206
456 | Dhankal | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 207
457 | Dhankal | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 208
458 | Dhankal | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 209
459 | Dhankal | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 210
460 | Dhankal | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 211
461 | Dhankal | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 212
462 | Dhankal | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 213
463 | Dhankal | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 214
464 | Dhankal | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 215
465 | Dhankal | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 216
466 | Dhankal | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 217
467 | Dhankal | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 218
468 | Dhankal | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 219
469 | Dhankal | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
470 | Dhankal | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
471 | Dhankal | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
472 | Dhankal | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
473 | Dhankal | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
474 | Dhankal | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5188
475 | Dhankal | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5189
476 | Dhankal | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5190
477 | Dhankal | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5191
478 | Dhankal | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5192
479 | Dhankal | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5193
480 | Dhankal | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5194
481 | Dhankal | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5195
482 | Dhankal | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5196
483 | Dhankal | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5197
484 | Dhankal | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5198
485 | Dhankal | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5199
486 | Dhankal | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5200
487 | Dhankal | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5201
488 | Dhankal | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5202
489 | Dhankal | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5203
490 | Dhankal | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5204
491 | 3rd Feeder | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 220
492 | 3rd Feeder | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 221
493 | 3rd Feeder | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 222
494 | 3rd Feeder | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 223
495 | 3rd Feeder | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 224
496 | 3rd Feeder | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 225
497 | 3rd Feeder | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 226
498 | 3rd Feeder | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 227
499 | 3rd Feeder | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 228
500 | 3rd Feeder | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 229
501 | 3rd Feeder | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 230
502 | 3rd Feeder | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 231
503 | 3rd Feeder | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 232
504 | 3rd Feeder | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 233
505 | 3rd Feeder | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
506 | 3rd Feeder | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
507 | 3rd Feeder | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
508 | 3rd Feeder | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
509 | 3rd Feeder | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
510 | 3rd Feeder | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5205
511 | 3rd Feeder | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5206
512 | 3rd Feeder | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5207
513 | 3rd Feeder | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5208
514 | 3rd Feeder | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5209
515 | 3rd Feeder | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5210
516 | 3rd Feeder | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5211
517 | 3rd Feeder | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5212
518 | 3rd Feeder | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5213
519 | 3rd Feeder | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5214
520 | 3rd Feeder | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5215
521 | 3rd Feeder | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5216
522 | 3rd Feeder | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5217
523 | 3rd Feeder | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5218
524 | 3rd Feeder | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5219
525 | 3rd Feeder | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5220
526 | 3rd Feeder | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5221
527 | Incomer-1 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 234
528 | Incomer-1 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 235
529 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 236
530 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 237
531 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 238
532 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 239
533 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 240
534 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 241
535 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 242
536 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 243
537 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 244
538 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 245
539 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 246
540 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
541 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
542 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
543 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13046
544 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13047
545 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5222
546 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5223
547 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5224
548 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5225
549 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5226
550 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5227
551 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5228
552 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5229
553 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5230
554 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5231
555 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5232
556 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5233
557 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5234
558 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5235
559 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5236
560 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5237
561 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5238
562 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 247
563 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 248
564 | BUSCOUPLER-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 249
565 | BUSCOUPLER-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 250
566 | BUSCOUPLER-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 251
567 | BUSCOUPLER-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 252
568 | BUSCOUPLER-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 253
569 | BUSCOUPLER-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 254 |  |  |  | AC CMR to be used
570 | BUSCOUPLER-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 255
571 | BUSCOUPLER-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 256
572 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10013
573 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10013
574 | Incomer-2 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 257
575 | Incomer-2 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 258
576 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 259
577 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 260
578 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 261
579 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 262
580 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 263
581 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 264
582 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 265
583 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 266
584 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 267
585 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 268
586 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 269
587 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
588 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
589 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
590 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13049
591 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13050
592 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5239
593 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5240
594 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5241
595 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5242
596 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5243
597 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5244
598 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5245
599 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5246
600 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5247
601 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5248
602 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5249
603 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5250
604 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5251
605 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5252
606 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5253
607 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5254
608 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5255
609 | Mission Bazar | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 270
610 | Mission Bazar | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 271
611 | Mission Bazar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 272
612 | Mission Bazar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 273
613 | Mission Bazar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 274
614 | Mission Bazar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 275
615 | Mission Bazar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 276
616 | Mission Bazar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 277
617 | Mission Bazar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 278
618 | Mission Bazar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 279
619 | Mission Bazar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 280
620 | Mission Bazar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 281
621 | Mission Bazar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 282
622 | Mission Bazar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 283
623 | Mission Bazar | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
624 | Mission Bazar | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
625 | Mission Bazar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
626 | Mission Bazar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
627 | Mission Bazar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
628 | Mission Bazar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5256
629 | Mission Bazar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5257
630 | Mission Bazar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5258
631 | Mission Bazar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5259
632 | Mission Bazar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5260
633 | Mission Bazar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5261
634 | Mission Bazar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5262
635 | Mission Bazar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5263
636 | Mission Bazar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5264
637 | Mission Bazar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5265
638 | Mission Bazar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5266
639 | Mission Bazar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5267
640 | Mission Bazar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5268
641 | Mission Bazar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5269
642 | Mission Bazar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5270
643 | Mission Bazar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5271
644 | Mission Bazar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5272
645 | Village | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 284
646 | Village | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 285
647 | Village | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 286
648 | Village | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 287
649 | Village | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 288
650 | Village | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 289
651 | Village | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 290
652 | Village | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 291
653 | Village | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 292
654 | Village | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 293
655 | Village | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 294
656 | Village | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 295
657 | Village | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 296
658 | Village | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 297
659 | Village | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
660 | Village | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
661 | Village | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
662 | Village | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
663 | Village | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
664 | Village | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5273
665 | Village | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5274
666 | Village | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5275
667 | Village | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5276
668 | Village | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5277
669 | Village | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5278
670 | Village | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5279
671 | Village | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5280
672 | Village | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5281
673 | Village | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5282
674 | Village | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5283
675 | Village | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5284
676 | Village | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5285
677 | Village | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5286
678 | Village | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5287
679 | Village | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5288
680 | Village | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5289
681 | Jayangra-3 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 298
682 | Jayangra-3 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 299
683 | Jayangra-3 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 300
684 | Jayangra-3 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 301
685 | Jayangra-3 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 302
686 | Jayangra-3 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 303
687 | Jayangra-3 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 304
688 | Jayangra-3 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 305
689 | Jayangra-3 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 306
690 | Jayangra-3 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 307
691 | Jayangra-3 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 308
692 | Jayangra-3 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 309
693 | Jayangra-3 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 310
694 | Jayangra-3 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 311
695 | Jayangra-3 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
696 | Jayangra-3 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
697 | Jayangra-3 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
698 | Jayangra-3 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
699 | Jayangra-3 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
700 | Jayangra-3 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5290
701 | Jayangra-3 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5291
702 | Jayangra-3 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5292
703 | Jayangra-3 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5293
704 | Jayangra-3 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5294
705 | Jayangra-3 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5295
706 | Jayangra-3 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5296
707 | Jayangra-3 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5297
708 | Jayangra-3 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5298
709 | Jayangra-3 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5299
710 | Jayangra-3 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5300
711 | Jayangra-3 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5301
712 | Jayangra-3 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5302
713 | Jayangra-3 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5303
714 | Jayangra-3 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5304
715 | Jayangra-3 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5305
716 | Jayangra-3 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5306
717 | Spare-2 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 312
718 | Spare-2 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 313
719 | Spare-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 314
720 | Spare-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 315
721 | Spare-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 316
722 | Spare-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 317
723 | Spare-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 318
724 | Spare-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 319
725 | Spare-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 320
726 | Spare-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 321
727 | Spare-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 322
728 | Spare-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 323
729 | Spare-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 324
730 | Spare-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 325
731 | Spare-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
732 | Spare-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
733 | Spare-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
734 | Spare-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
735 | Spare-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
736 | Spare-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5307
737 | Spare-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5308
738 | Spare-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5309
739 | Spare-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5310
740 | Spare-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5311
741 | Spare-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5312
742 | Spare-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5313
743 | Spare-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5314
744 | Spare-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5315
745 | Spare-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5316
746 | Spare-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5317
747 | Spare-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5318
748 | Spare-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5319
749 | Spare-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5320
750 | Spare-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5321
751 | Spare-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5322
752 | Spare-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5323
753 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 326
754 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 327
755 | BUSCOUPLER-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 328
756 | BUSCOUPLER-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 329
757 | BUSCOUPLER-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 330
758 | BUSCOUPLER-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 331
759 | BUSCOUPLER-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 332
760 | BUSCOUPLER-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 333 |  |  |  | AC CMR to be used
761 | BUSCOUPLER-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 334
762 | BUSCOUPLER-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 335
763 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10019
764 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10019
765 | Helabattala-1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 336
766 | Helabattala-1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 337
767 | Helabattala-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 338
768 | Helabattala-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 339
769 | Helabattala-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 340
770 | Helabattala-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 341
771 | Helabattala-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 342
772 | Helabattala-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 343
773 | Helabattala-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 344
774 | Helabattala-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 345
775 | Helabattala-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 346
776 | Helabattala-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 347
777 | Helabattala-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 348
778 | Helabattala-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 349
779 | Helabattala-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
780 | Helabattala-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
781 | Helabattala-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
782 | Helabattala-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
783 | Helabattala-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
784 | Helabattala-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5324
785 | Helabattala-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5325
786 | Helabattala-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5326
787 | Helabattala-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5327
788 | Helabattala-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5328
789 | Helabattala-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5329
790 | Helabattala-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5330
791 | Helabattala-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5331
792 | Helabattala-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5332
793 | Helabattala-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5333
794 | Helabattala-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5334
795 | Helabattala-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5335
796 | Helabattala-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5336
797 | Helabattala-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5337
798 | Helabattala-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5338
799 | Helabattala-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5339
800 | Helabattala-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5340
801 | Jayangra-2 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 350
802 | Jayangra-2 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 351
803 | Jayangra-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 352
804 | Jayangra-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 353
805 | Jayangra-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 354
806 | Jayangra-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 355
807 | Jayangra-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 356
808 | Jayangra-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 357
809 | Jayangra-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 358
810 | Jayangra-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 359
811 | Jayangra-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 360
812 | Jayangra-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 361
813 | Jayangra-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 362
814 | Jayangra-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 363
815 | Jayangra-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
816 | Jayangra-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
817 | Jayangra-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
818 | Jayangra-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
819 | Jayangra-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
820 | Jayangra-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5341
821 | Jayangra-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5342
822 | Jayangra-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5343
823 | Jayangra-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5344
824 | Jayangra-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5345
825 | Jayangra-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5346
826 | Jayangra-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5347
827 | Jayangra-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5348
828 | Jayangra-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5349
829 | Jayangra-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5350
830 | Jayangra-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5351
831 | Jayangra-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5352
832 | Jayangra-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5353
833 | Jayangra-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5354
834 | Jayangra-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5355
835 | Jayangra-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5356
836 | Jayangra-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5357
837 | Baroaritala | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 364
838 | Baroaritala | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 365
839 | Baroaritala | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 366
840 | Baroaritala | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 367
841 | Baroaritala | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 368
842 | Baroaritala | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 369
843 | Baroaritala | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 370
844 | Baroaritala | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 371
845 | Baroaritala | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 372
846 | Baroaritala | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 373
847 | Baroaritala | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 374
848 | Baroaritala | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 375
849 | Baroaritala | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 376
850 | Baroaritala | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 377
851 | Baroaritala | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
852 | Baroaritala | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
853 | Baroaritala | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
854 | Baroaritala | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
855 | Baroaritala | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
856 | Baroaritala | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5358
857 | Baroaritala | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5359
858 | Baroaritala | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5360
859 | Baroaritala | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5361
860 | Baroaritala | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5362
861 | Baroaritala | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5363
862 | Baroaritala | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5364
863 | Baroaritala | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5365
864 | Baroaritala | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5366
865 | Baroaritala | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5367
866 | Baroaritala | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5368
867 | Baroaritala | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5369
868 | Baroaritala | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5370
869 | Baroaritala | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5371
870 | Baroaritala | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5372
871 | Baroaritala | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5373
872 | Baroaritala | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5374
873 | Spare-3 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 378
874 | Spare-3 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 379
875 | Spare-3 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 380
876 | Spare-3 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 381
877 | Spare-3 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 382
878 | Spare-3 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 383
879 | Spare-3 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 384
880 | Spare-3 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 385
881 | Spare-3 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 386
882 | Spare-3 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 387
883 | Spare-3 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 388
884 | Spare-3 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 389
885 | Spare-3 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 390
886 | Spare-3 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 391
887 | Spare-3 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
888 | Spare-3 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
889 | Spare-3 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
890 | Spare-3 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
891 | Spare-3 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
892 | Spare-3 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5375
893 | Spare-3 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5376
894 | Spare-3 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5377
895 | Spare-3 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5378
896 | Spare-3 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5379
897 | Spare-3 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5380
898 | Spare-3 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5381
899 | Spare-3 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5382
900 | Spare-3 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5383
901 | Spare-3 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5384
902 | Spare-3 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5385
903 | Spare-3 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5386
904 | Spare-3 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5387
905 | Spare-3 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5388
906 | Spare-3 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5389
907 | Spare-3 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5390
908 | Spare-3 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5391
909 | Incoming-3 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 392
910 | Incoming-3 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 393
911 | Incoming-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 394
912 | Incoming-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 395
913 | Incoming-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 396
914 | Incoming-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 397
915 | Incoming-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 398
916 | Incoming-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 399
917 | Incoming-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 400
918 | Incoming-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 401
919 | Incoming-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 402
920 | Incoming-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 403
921 | Incoming-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 404
922 | Incoming-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
923 | Incoming-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
924 | Incoming-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
925 | Incoming-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13076
926 | Incoming-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13077
927 | Incoming-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5392
928 | Incoming-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5393
929 | Incoming-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5394
930 | Incoming-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5395
931 | Incoming-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5396
932 | Incoming-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5397
933 | Incoming-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5398
934 | Incoming-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5399
935 | Incoming-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5400
936 | Incoming-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5401
937 | Incoming-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5402
938 | Incoming-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5403
939 | Incoming-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5404
940 | Incoming-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5405
941 | Incoming-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5406
942 | Incoming-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5407
943 | Incoming-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5408
944 | BUSCOUPLER-3 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 405
945 | BUSCOUPLER-3 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 406
946 | BUSCOUPLER-3 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 407
947 | BUSCOUPLER-3 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 408
948 | BUSCOUPLER-3 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 409
949 | BUSCOUPLER-3 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 410
950 | BUSCOUPLER-3 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 411
951 | BUSCOUPLER-3 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 412 |  |  |  | AC CMR to be used
952 | BUSCOUPLER-3 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 413
953 | BUSCOUPLER-3 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 414
954 | BUSCOUPLER-3 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10025
955 | BUSCOUPLER-3 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10025
956 | Incoming-4 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 415
957 | Incoming-4 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 416
958 | Incoming-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 417
959 | Incoming-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 418
960 | Incoming-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 419
961 | Incoming-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 420
962 | Incoming-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 421
963 | Incoming-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 422
964 | Incoming-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 423
965 | Incoming-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 424
966 | Incoming-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 425
967 | Incoming-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 426
968 | Incoming-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 427
969 | Incoming-4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
970 | Incoming-4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
971 | Incoming-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
972 | Incoming-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13079
973 | Incoming-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13080
974 | Incoming-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5409
975 | Incoming-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5410
976 | Incoming-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5411
977 | Incoming-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5412
978 | Incoming-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5413
979 | Incoming-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5414
980 | Incoming-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5415
981 | Incoming-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5416
982 | Incoming-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5417
983 | Incoming-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5418
984 | Incoming-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5419
985 | Incoming-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5420
986 | Incoming-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5421
987 | Incoming-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5422
988 | Incoming-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5423
989 | Incoming-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5424
990 | Incoming-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5425
991 | 4th Feeder | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 428
992 | 4th Feeder | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 429
993 | 4th Feeder | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 430
994 | 4th Feeder | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 431
995 | 4th Feeder | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 432
996 | 4th Feeder | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 433
997 | 4th Feeder | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 434
998 | 4th Feeder | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 435
999 | 4th Feeder | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 436
1000 | 4th Feeder | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 437
1001 | 4th Feeder | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 438
1002 | 4th Feeder | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 439
1003 | 4th Feeder | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 440
1004 | 4th Feeder | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 441
1005 | 4th Feeder | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10027
1006 | 4th Feeder | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10027
1007 | 4th Feeder | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
1008 | 4th Feeder | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13082
1009 | 4th Feeder | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13083
1010 | 4th Feeder | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5426
1011 | 4th Feeder | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5427
1012 | 4th Feeder | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5428
1013 | 4th Feeder | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5429
1014 | 4th Feeder | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5430
1015 | 4th Feeder | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5431
1016 | 4th Feeder | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5432
1017 | 4th Feeder | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5433
1018 | 4th Feeder | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5434
1019 | 4th Feeder | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5435
1020 | 4th Feeder | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5436
1021 | 4th Feeder | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5437
1022 | 4th Feeder | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5438
1023 | 4th Feeder | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5439
1024 | 4th Feeder | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5440
1025 | 4th Feeder | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5441
1026 | 4th Feeder | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5442
1027 | Helabattala-2 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 442
1028 | Helabattala-2 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 443
1029 | Helabattala-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 444
1030 | Helabattala-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 445
1031 | Helabattala-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 446
1032 | Helabattala-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 447
1033 | Helabattala-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 448
1034 | Helabattala-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 449
1035 | Helabattala-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 450
1036 | Helabattala-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 451
1037 | Helabattala-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 452
1038 | Helabattala-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 453
1039 | Helabattala-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 454
1040 | Helabattala-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 455
1041 | Helabattala-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10028
1042 | Helabattala-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10028
1043 | Helabattala-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1044 | Helabattala-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1045 | Helabattala-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13086
1046 | Helabattala-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5443
1047 | Helabattala-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5444
1048 | Helabattala-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5445
1049 | Helabattala-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5446
1050 | Helabattala-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5447
1051 | Helabattala-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5448
1052 | Helabattala-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5449
1053 | Helabattala-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5450
1054 | Helabattala-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5451
1055 | Helabattala-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5452
1056 | Helabattala-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5453
1057 | Helabattala-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5454
1058 | Helabattala-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5455
1059 | Helabattala-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5456
1060 | Helabattala-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5457
1061 | Helabattala-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5458
1062 | Helabattala-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5459
1063 | Jayangra-1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 456
1064 | Jayangra-1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 457
1065 | Jayangra-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 458
1066 | Jayangra-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 459
1067 | Jayangra-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 460
1068 | Jayangra-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 461
1069 | Jayangra-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 462
1070 | Jayangra-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 463
1071 | Jayangra-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 464
1072 | Jayangra-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 465
1073 | Jayangra-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 466
1074 | Jayangra-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 467
1075 | Jayangra-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 468
1076 | Jayangra-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 469
1077 | Jayangra-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10029
1078 | Jayangra-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10029
1079 | Jayangra-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1080 | Jayangra-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1081 | Jayangra-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13089
1082 | Jayangra-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5460
1083 | Jayangra-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5461
1084 | Jayangra-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5462
1085 | Jayangra-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5463
1086 | Jayangra-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5464
1087 | Jayangra-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5465
1088 | Jayangra-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5466
1089 | Jayangra-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5467
1090 | Jayangra-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5468
1091 | Jayangra-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5469
1092 | Jayangra-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5470
1093 | Jayangra-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5471
1094 | Jayangra-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5472
1095 | Jayangra-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5473
1096 | Jayangra-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5474
1097 | Jayangra-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5475
1098 | Jayangra-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5476
1099 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 470
1100 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 471
1101 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 472
1102 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 473
1103 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 474
1104 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 475
1105 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 476
1106 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 477
1107 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 478
1108 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 479
1109 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 480
1110 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 481
1111 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1112 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1113 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13092
1114 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10030
1115 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10030
1116 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5477
1117 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5478
1118 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5479
1119 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5480
1120 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5481
1121 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5482
1122 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5483
1123 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5484
1124 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5485
1125 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5486
1126 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5487
1127 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5488
1128 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5489
1129 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5490
1130 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5491
1131 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5492
1132 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5493
1133 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5494
1134 | Bagjola-Chandiberia Interconnector | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5495