## Signal List
SCADA/Distribution Management System (DMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Sub-Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Sub-Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | Transformer-4 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 112
209 | Transformer-4 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 113
210 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 114
211 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 115
212 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 116
213 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 117
214 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 118
215 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 119
216 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 120
217 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 121
218 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 122
219 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 123
220 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 124
221 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 125
222 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 126
223 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 127
224 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 128
225 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 129
226 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 130
227 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 131
228 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 132
229 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 133
230 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 134
231 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 135
232 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
233 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
234 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
235 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
236 | Transformer-4 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
237 | Transformer-4 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
238 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5068
239 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5069
240 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5070
241 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5071
242 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5072
243 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5073
244 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5074
245 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5075
246 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5076
247 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5077
248 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5078
249 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5079
250 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5080
251 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5081
252 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5082
253 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
254 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
255 | Transformer-4 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 136
256 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 137
257 | Transformer-4 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 138 |  |  |  | AC CMR to be used
258 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 139
259 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 140
260 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 141
261 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 142
262 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 143
263 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
264 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
265 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5085
266 | Transformer-4 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5086
267 | Transformer-4 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5087
268 | Mahispota-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 144
269 | Mahispota-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 145
270 | Mahispota-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 146
271 | Mahispota-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 147
272 | Mahispota-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 148
273 | Mahispota-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 149
274 | Mahispota-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 150
275 | Mahispota-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 151
276 | Mahispota-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 152
277 | Mahispota-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 153
278 | Mahispota-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 154
279 | Mahispota-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 155
280 | Mahispota-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
281 | Mahispota-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
282 | Mahispota-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
283 | Mahispota-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
284 | Mahispota-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
285 | Mahispota-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5088
286 | Mahispota-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5089
287 | Mahispota-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5090
288 | Mahispota-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5091
289 | Mahispota-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5092
290 | Mahispota-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5093
291 | Mahispota-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5094
292 | Mahispota-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5095
293 | Mahispota-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5096
294 | Mahispota-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5097
295 | Mahispota-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5098
296 | Mahispota-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5099
297 | Mahispota-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5100
298 | Mahispota-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5101
299 | Mahispota-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5102
300 | Mahispota-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5103
301 | Mahispota-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5104
302 | Mahispota-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5105
303 | Mahispota-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5106
304 | Mahispota-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 156
305 | Mahispota-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 157
306 | Mahispota-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 158
307 | Mahispota-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 159
308 | Mahispota-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 160
309 | Mahispota-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 161
310 | Mahispota-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 162
311 | Mahispota-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 163
312 | Mahispota-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 164
313 | Mahispota-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 165
314 | Mahispota-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 166
315 | Mahispota-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 167
316 | Mahispota-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
317 | Mahispota-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
318 | Mahispota-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13029
319 | Mahispota-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
320 | Mahispota-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
321 | Mahispota-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5107
322 | Mahispota-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5108
323 | Mahispota-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5109
324 | Mahispota-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5110
325 | Mahispota-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5111
326 | Mahispota-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5112
327 | Mahispota-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5113
328 | Mahispota-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5114
329 | Mahispota-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5115
330 | Mahispota-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5116
331 | Mahispota-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5117
332 | Mahispota-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5118
333 | Mahispota-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5119
334 | Mahispota-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5120
335 | Mahispota-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5121
336 | Mahispota-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5122
337 | Mahispota-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5123
338 | Mahispota-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5124
339 | Mahispota-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5125
340 | Mahispota-3 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 168
341 | Mahispota-3 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 169
342 | Mahispota-3 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 170
343 | Mahispota-3 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 171
344 | Mahispota-3 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 172
345 | Mahispota-3 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 173
346 | Mahispota-3 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 174
347 | Mahispota-3 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 175
348 | Mahispota-3 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 176
349 | Mahispota-3 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 177
350 | Mahispota-3 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 178
351 | Mahispota-3 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 179
352 | Mahispota-3 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
353 | Mahispota-3 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13031
354 | Mahispota-3 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13032
355 | Mahispota-3 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
356 | Mahispota-3 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
357 | Mahispota-3 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5126
358 | Mahispota-3 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5127
359 | Mahispota-3 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5128
360 | Mahispota-3 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5129
361 | Mahispota-3 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5130
362 | Mahispota-3 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5131
363 | Mahispota-3 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5132
364 | Mahispota-3 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5133
365 | Mahispota-3 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5134
366 | Mahispota-3 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5135
367 | Mahispota-3 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5136
368 | Mahispota-3 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5137
369 | Mahispota-3 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5138
370 | Mahispota-3 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5139
371 | Mahispota-3 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5140
372 | Mahispota-3 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5141
373 | Mahispota-3 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5142
374 | Mahispota-3 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5143
375 | Mahispota-3 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5144
376 | W.T.P | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 180
377 | W.T.P | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 181
378 | W.T.P | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 182
379 | W.T.P | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 183
380 | W.T.P | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 184
381 | W.T.P | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 185
382 | W.T.P | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 186
383 | W.T.P | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 187
384 | W.T.P | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 188
385 | W.T.P | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 189
386 | W.T.P | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 190
387 | W.T.P | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 191
388 | W.T.P | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
389 | W.T.P | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
390 | W.T.P | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13035
391 | W.T.P | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
392 | W.T.P | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
393 | W.T.P | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5145
394 | W.T.P | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5146
395 | W.T.P | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5147
396 | W.T.P | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5148
397 | W.T.P | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5149
398 | W.T.P | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5150
399 | W.T.P | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5151
400 | W.T.P | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5152
401 | W.T.P | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5153
402 | W.T.P | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5154
403 | W.T.P | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5155
404 | W.T.P | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5156
405 | W.T.P | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5157
406 | W.T.P | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5158
407 | W.T.P | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5159
408 | W.T.P | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5160
409 | W.T.P | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5161
410 | W.T.P | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5162
411 | W.T.P | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5163
412 | Mahispota-4 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 192
413 | Mahispota-4 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 193
414 | Mahispota-4 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 194
415 | Mahispota-4 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 195
416 | Mahispota-4 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 196
417 | Mahispota-4 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 197
418 | Mahispota-4 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 198
419 | Mahispota-4 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 199
420 | Mahispota-4 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 200
421 | Mahispota-4 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 201
422 | Mahispota-4 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 202
423 | Mahispota-4 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 203
424 | Mahispota-4 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
425 | Mahispota-4 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
426 | Mahispota-4 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13038
427 | Mahispota-4 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
428 | Mahispota-4 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
429 | Mahispota-4 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5164
430 | Mahispota-4 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5165
431 | Mahispota-4 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5166
432 | Mahispota-4 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5167
433 | Mahispota-4 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5168
434 | Mahispota-4 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5169
435 | Mahispota-4 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5170
436 | Mahispota-4 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5171
437 | Mahispota-4 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5172
438 | Mahispota-4 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5173
439 | Mahispota-4 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5174
440 | Mahispota-4 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5175
441 | Mahispota-4 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5176
442 | Mahispota-4 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5177
443 | Mahispota-4 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5178
444 | Mahispota-4 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5179
445 | Mahispota-4 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5180
446 | Mahispota-4 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5181
447 | Mahispota-4 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5182
448 | Spare | 33kV | I/C + Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 204
449 | Spare | 33kV | I/C + Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 205
450 | Spare | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 206
451 | Spare | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 207
452 | Spare | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 208
453 | Spare | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 209
454 | Spare | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 210
455 | Spare | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 211
456 | Spare | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 212
457 | Spare | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 213
458 | Spare | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 214
459 | Spare | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 215
460 | Spare | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
461 | Spare | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
462 | Spare | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13041
463 | Spare | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
464 | Spare | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
465 | Spare | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5183
466 | Spare | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5184
467 | Spare | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5185
468 | Spare | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5186
469 | Spare | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5187
470 | Spare | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5188
471 | Spare | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5189
472 | Spare | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5190
473 | Spare | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5191
474 | Spare | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5192
475 | Spare | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5193
476 | Spare | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5194
477 | Spare | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5195
478 | Spare | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5196
479 | Spare | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5197
480 | Spare | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5198
481 | Spare | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5199
482 | Spare | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5200
483 | Spare | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5201
484 | Panihara | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 216
485 | Panihara | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 217
486 | Panihara | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 218
487 | Panihara | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 219
488 | Panihara | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 220
489 | Panihara | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 221
490 | Panihara | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 222
491 | Panihara | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 223
492 | Panihara | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 224
493 | Panihara | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 225
494 | Panihara | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 226
495 | Panihara | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 227
496 | Panihara | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 228
497 | Panihara | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 229
498 | Panihara | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
499 | Panihara | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
500 | Panihara | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
501 | Panihara | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
502 | Panihara | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
503 | Panihara | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5202
504 | Panihara | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5203
505 | Panihara | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5204
506 | Panihara | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5205
507 | Panihara | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5206
508 | Panihara | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5207
509 | Panihara | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5208
510 | Panihara | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5209
511 | Panihara | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5210
512 | Panihara | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5211
513 | Panihara | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5212
514 | Panihara | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5213
515 | Panihara | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5214
516 | Panihara | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5215
517 | Panihara | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5216
518 | Panihara | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5217
519 | Panihara | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5218
520 | Incomer-4 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 230
521 | Incomer-4 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 231
522 | Incomer-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 232
523 | Incomer-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 233
524 | Incomer-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 234
525 | Incomer-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 235
526 | Incomer-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 236
527 | Incomer-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 237
528 | Incomer-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 238
529 | Incomer-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 239
530 | Incomer-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 240
531 | Incomer-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 241
532 | Incomer-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 242
533 | Incomer-4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
534 | Incomer-4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
535 | Incomer-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
536 | Incomer-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13046
537 | Incomer-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13047
538 | Incomer-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5219
539 | Incomer-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5220
540 | Incomer-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5221
541 | Incomer-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5222
542 | Incomer-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5223
543 | Incomer-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5224
544 | Incomer-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5225
545 | Incomer-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5226
546 | Incomer-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5227
547 | Incomer-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5228
548 | Incomer-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5229
549 | Incomer-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5230
550 | Incomer-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5231
551 | Incomer-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5232
552 | Incomer-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5233
553 | Incomer-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5234
554 | Incomer-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5235
555 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 243
556 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 244
557 | Bus Coupler-3 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 245
558 | Bus Coupler-3 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 246
559 | Bus Coupler-3 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 247
560 | Bus Coupler-3 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 248
561 | Bus Coupler-3 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 249
562 | Bus Coupler-3 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 250 |  |  |  | AC CMR to be used
563 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 251
564 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 252
565 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10013
566 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10013
567 | Wind mere | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 253
568 | Wind mere | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 254
569 | Wind mere | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 255
570 | Wind mere | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 256
571 | Wind mere | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 257
572 | Wind mere | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 258
573 | Wind mere | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 259
574 | Wind mere | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 260
575 | Wind mere | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 261
576 | Wind mere | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 262
577 | Wind mere | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 263
578 | Wind mere | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 264
579 | Wind mere | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 265
580 | Wind mere | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 266
581 | Wind mere | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
582 | Wind mere | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
583 | Wind mere | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
584 | Wind mere | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
585 | Wind mere | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
586 | Wind mere | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5236
587 | Wind mere | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5237
588 | Wind mere | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5238
589 | Wind mere | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5239
590 | Wind mere | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5240
591 | Wind mere | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5241
592 | Wind mere | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5242
593 | Wind mere | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5243
594 | Wind mere | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5244
595 | Wind mere | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5245
596 | Wind mere | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5246
597 | Wind mere | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5247
598 | Wind mere | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5248
599 | Wind mere | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5249
600 | Wind mere | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5250
601 | Wind mere | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5251
602 | Wind mere | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5252
603 | Masunda | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 267
604 | Masunda | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 268
605 | Masunda | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 269
606 | Masunda | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 270
607 | Masunda | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 271
608 | Masunda | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 272
609 | Masunda | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 273
610 | Masunda | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 274
611 | Masunda | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 275
612 | Masunda | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 276
613 | Masunda | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 277
614 | Masunda | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 278
615 | Masunda | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 279
616 | Masunda | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 280
617 | Masunda | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
618 | Masunda | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
619 | Masunda | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
620 | Masunda | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
621 | Masunda | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
622 | Masunda | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5253
623 | Masunda | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5254
624 | Masunda | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5255
625 | Masunda | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5256
626 | Masunda | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5257
627 | Masunda | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5258
628 | Masunda | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5259
629 | Masunda | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5260
630 | Masunda | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5261
631 | Masunda | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5262
632 | Masunda | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5263
633 | Masunda | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5264
634 | Masunda | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5265
635 | Masunda | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5266
636 | Masunda | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5267
637 | Masunda | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5268
638 | Masunda | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5269
639 | Kalibari | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 281
640 | Kalibari | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 282
641 | Kalibari | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 283
642 | Kalibari | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 284
643 | Kalibari | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 285
644 | Kalibari | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 286
645 | Kalibari | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 287
646 | Kalibari | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 288
647 | Kalibari | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 289
648 | Kalibari | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 290
649 | Kalibari | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 291
650 | Kalibari | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 292
651 | Kalibari | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 293
652 | Kalibari | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 294
653 | Kalibari | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
654 | Kalibari | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
655 | Kalibari | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
656 | Kalibari | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
657 | Kalibari | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
658 | Kalibari | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5270
659 | Kalibari | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5271
660 | Kalibari | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5272
661 | Kalibari | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5273
662 | Kalibari | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5274
663 | Kalibari | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5275
664 | Kalibari | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5276
665 | Kalibari | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5277
666 | Kalibari | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5278
667 | Kalibari | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5279
668 | Kalibari | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5280
669 | Kalibari | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5281
670 | Kalibari | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5282
671 | Kalibari | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5283
672 | Kalibari | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5284
673 | Kalibari | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5285
674 | Kalibari | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5286
675 | New barrackpore | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 295
676 | New barrackpore | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 296
677 | New barrackpore | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 297
678 | New barrackpore | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 298
679 | New barrackpore | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 299
680 | New barrackpore | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 300
681 | New barrackpore | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 301
682 | New barrackpore | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 302
683 | New barrackpore | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 303
684 | New barrackpore | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 304
685 | New barrackpore | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 305
686 | New barrackpore | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 306
687 | New barrackpore | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 307
688 | New barrackpore | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 308
689 | New barrackpore | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
690 | New barrackpore | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
691 | New barrackpore | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
692 | New barrackpore | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
693 | New barrackpore | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
694 | New barrackpore | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5287
695 | New barrackpore | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5288
696 | New barrackpore | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5289
697 | New barrackpore | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5290
698 | New barrackpore | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5291
699 | New barrackpore | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5292
700 | New barrackpore | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5293
701 | New barrackpore | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5294
702 | New barrackpore | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5295
703 | New barrackpore | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5296
704 | New barrackpore | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5297
705 | New barrackpore | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5298
706 | New barrackpore | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5299
707 | New barrackpore | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5300
708 | New barrackpore | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5301
709 | New barrackpore | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5302
710 | New barrackpore | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5303
711 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 309
712 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 310
713 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 311
714 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 312
715 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 313
716 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 314
717 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 315
718 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 316
719 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 317
720 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 318
721 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 319
722 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 320
723 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 321
724 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
725 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
726 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
727 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13061
728 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13062
729 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5304
730 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5305
731 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5306
732 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5307
733 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5308
734 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5309
735 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5310
736 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5311
737 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5312
738 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5313
739 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5314
740 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5315
741 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5316
742 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5317
743 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5318
744 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5319
745 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5320
746 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 322
747 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 323
748 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 324
749 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 325
750 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 326
751 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 327
752 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 328
753 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 329 |  |  |  | AC CMR to be used
754 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 330
755 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 331
756 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10019
757 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10019
758 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 332
759 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 333
760 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 334
761 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 335
762 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 336
763 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 337
764 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 338
765 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 339
766 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 340
767 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 341
768 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 342
769 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 343
770 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 344
771 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
772 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
773 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
774 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13064
775 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13065
776 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5321
777 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5322
778 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5323
779 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5324
780 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5325
781 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5326
782 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5327
783 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5328
784 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5329
785 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5330
786 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5331
787 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5332
788 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5333
789 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5334
790 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5335
791 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5336
792 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5337
793 | Deshbandhu | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 345
794 | Deshbandhu | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 346
795 | Deshbandhu | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 347
796 | Deshbandhu | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 348
797 | Deshbandhu | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 349
798 | Deshbandhu | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 350
799 | Deshbandhu | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 351
800 | Deshbandhu | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 352
801 | Deshbandhu | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 353
802 | Deshbandhu | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 354
803 | Deshbandhu | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 355
804 | Deshbandhu | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 356
805 | Deshbandhu | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 357
806 | Deshbandhu | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 358
807 | Deshbandhu | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
808 | Deshbandhu | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
809 | Deshbandhu | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
810 | Deshbandhu | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
811 | Deshbandhu | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
812 | Deshbandhu | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5338
813 | Deshbandhu | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5339
814 | Deshbandhu | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5340
815 | Deshbandhu | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5341
816 | Deshbandhu | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5342
817 | Deshbandhu | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5343
818 | Deshbandhu | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5344
819 | Deshbandhu | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5345
820 | Deshbandhu | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5346
821 | Deshbandhu | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5347
822 | Deshbandhu | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5348
823 | Deshbandhu | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5349
824 | Deshbandhu | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5350
825 | Deshbandhu | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5351
826 | Deshbandhu | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5352
827 | Deshbandhu | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5353
828 | Deshbandhu | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5354
829 | Madhyamgram | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 359
830 | Madhyamgram | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 360
831 | Madhyamgram | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 361
832 | Madhyamgram | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 362
833 | Madhyamgram | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 363
834 | Madhyamgram | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 364
835 | Madhyamgram | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 365
836 | Madhyamgram | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 366
837 | Madhyamgram | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 367
838 | Madhyamgram | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 368
839 | Madhyamgram | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 369
840 | Madhyamgram | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 370
841 | Madhyamgram | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 371
842 | Madhyamgram | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 372
843 | Madhyamgram | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
844 | Madhyamgram | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
845 | Madhyamgram | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
846 | Madhyamgram | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
847 | Madhyamgram | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
848 | Madhyamgram | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5355
849 | Madhyamgram | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5356
850 | Madhyamgram | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5357
851 | Madhyamgram | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5358
852 | Madhyamgram | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5359
853 | Madhyamgram | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5360
854 | Madhyamgram | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5361
855 | Madhyamgram | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5362
856 | Madhyamgram | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5363
857 | Madhyamgram | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5364
858 | Madhyamgram | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5365
859 | Madhyamgram | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5366
860 | Madhyamgram | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5367
861 | Madhyamgram | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5368
862 | Madhyamgram | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5369
863 | Madhyamgram | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5370
864 | Madhyamgram | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5371
865 | Sharpur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 373
866 | Sharpur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 374
867 | Sharpur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 375
868 | Sharpur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 376
869 | Sharpur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 377
870 | Sharpur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 378
871 | Sharpur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 379
872 | Sharpur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 380
873 | Sharpur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 381
874 | Sharpur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 382
875 | Sharpur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 383
876 | Sharpur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 384
877 | Sharpur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 385
878 | Sharpur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 386
879 | Sharpur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
880 | Sharpur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
881 | Sharpur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
882 | Sharpur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
883 | Sharpur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
884 | Sharpur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5372
885 | Sharpur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5373
886 | Sharpur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5374
887 | Sharpur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5375
888 | Sharpur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5376
889 | Sharpur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5377
890 | Sharpur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5378
891 | Sharpur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5379
892 | Sharpur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5380
893 | Sharpur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5381
894 | Sharpur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5382
895 | Sharpur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5383
896 | Sharpur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5384
897 | Sharpur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5385
898 | Sharpur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5386
899 | Sharpur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5387
900 | Sharpur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5388
901 | Spare | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 387
902 | Spare | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 388
903 | Spare | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 389
904 | Spare | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 390
905 | Spare | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 391
906 | Spare | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 392
907 | Spare | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 393
908 | Spare | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 394
909 | Spare | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 395
910 | Spare | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 396
911 | Spare | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 397
912 | Spare | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 398
913 | Spare | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 399
914 | Spare | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 400
915 | Spare | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
916 | Spare | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
917 | Spare | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
918 | Spare | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13076
919 | Spare | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13077
920 | Spare | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5389
921 | Spare | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5390
922 | Spare | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5391
923 | Spare | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5392
924 | Spare | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5393
925 | Spare | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5394
926 | Spare | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5395
927 | Spare | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5396
928 | Spare | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5397
929 | Spare | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5398
930 | Spare | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5399
931 | Spare | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5400
932 | Spare | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5401
933 | Spare | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5402
934 | Spare | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5403
935 | Spare | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5404
936 | Spare | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5405
937 | Bus coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 401
938 | Bus coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 402
939 | Bus coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 403
940 | Bus coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 404
941 | Bus coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 405
942 | Bus coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 406
943 | Bus coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 407
944 | Bus coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 408 |  |  |  | AC CMR to be used
945 | Bus coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 409
946 | Bus coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 410
947 | Bus coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10025
948 | Bus coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10025
949 | Incomer-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 411
950 | Incomer-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 412
951 | Incomer-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 413
952 | Incomer-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 414
953 | Incomer-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 415
954 | Incomer-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 416
955 | Incomer-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 417
956 | Incomer-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 418
957 | Incomer-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 419
958 | Incomer-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 420
959 | Incomer-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 421
960 | Incomer-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 422
961 | Incomer-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 423
962 | Incomer-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
963 | Incomer-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
964 | Incomer-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
965 | Incomer-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13079
966 | Incomer-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13080
967 | Incomer-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5406
968 | Incomer-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5407
969 | Incomer-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5408
970 | Incomer-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5409
971 | Incomer-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5410
972 | Incomer-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5411
973 | Incomer-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5412
974 | Incomer-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5413
975 | Incomer-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5414
976 | Incomer-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5415
977 | Incomer-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5416
978 | Incomer-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5417
979 | Incomer-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5418
980 | Incomer-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5419
981 | Incomer-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5420
982 | Incomer-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5421
983 | Incomer-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5422
984 | Ganguly bari | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 424
985 | Ganguly bari | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 425
986 | Ganguly bari | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 426
987 | Ganguly bari | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 427
988 | Ganguly bari | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 428
989 | Ganguly bari | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 429
990 | Ganguly bari | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 430
991 | Ganguly bari | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 431
992 | Ganguly bari | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 432
993 | Ganguly bari | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 433
994 | Ganguly bari | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 434
995 | Ganguly bari | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 435
996 | Ganguly bari | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 436
997 | Ganguly bari | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 437
998 | Ganguly bari | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10027
999 | Ganguly bari | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10027
1000 | Ganguly bari | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
1001 | Ganguly bari | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13082
1002 | Ganguly bari | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13083
1003 | Ganguly bari | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5423
1004 | Ganguly bari | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5424
1005 | Ganguly bari | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5425
1006 | Ganguly bari | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5426
1007 | Ganguly bari | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5427
1008 | Ganguly bari | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5428
1009 | Ganguly bari | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5429
1010 | Ganguly bari | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5430
1011 | Ganguly bari | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5431
1012 | Ganguly bari | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5432
1013 | Ganguly bari | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5433
1014 | Ganguly bari | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5434
1015 | Ganguly bari | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5435
1016 | Ganguly bari | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5436
1017 | Ganguly bari | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5437
1018 | Ganguly bari | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5438
1019 | Ganguly bari | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5439
1020 | Industrial | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 438
1021 | Industrial | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 439
1022 | Industrial | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 440
1023 | Industrial | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 441
1024 | Industrial | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 442
1025 | Industrial | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 443
1026 | Industrial | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 444
1027 | Industrial | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 445
1028 | Industrial | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 446
1029 | Industrial | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 447
1030 | Industrial | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 448
1031 | Industrial | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 449
1032 | Industrial | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 450
1033 | Industrial | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 451
1034 | Industrial | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10028
1035 | Industrial | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10028
1036 | Industrial | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1037 | Industrial | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1038 | Industrial | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13086
1039 | Industrial | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5440
1040 | Industrial | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5441
1041 | Industrial | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5442
1042 | Industrial | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5443
1043 | Industrial | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5444
1044 | Industrial | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5445
1045 | Industrial | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5446
1046 | Industrial | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5447
1047 | Industrial | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5448
1048 | Industrial | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5449
1049 | Industrial | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5450
1050 | Industrial | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5451
1051 | Industrial | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5452
1052 | Industrial | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5453
1053 | Industrial | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5454
1054 | Industrial | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5455
1055 | Industrial | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5456
1056 | Sodepur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 452
1057 | Sodepur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 453
1058 | Sodepur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 454
1059 | Sodepur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 455
1060 | Sodepur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 456
1061 | Sodepur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 457
1062 | Sodepur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 458
1063 | Sodepur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 459
1064 | Sodepur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 460
1065 | Sodepur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 461
1066 | Sodepur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 462
1067 | Sodepur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 463
1068 | Sodepur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 464
1069 | Sodepur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 465
1070 | Sodepur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10029
1071 | Sodepur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10029
1072 | Sodepur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1073 | Sodepur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1074 | Sodepur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13089
1075 | Sodepur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5457
1076 | Sodepur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5458
1077 | Sodepur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5459
1078 | Sodepur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5460
1079 | Sodepur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5461
1080 | Sodepur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5462
1081 | Sodepur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5463
1082 | Sodepur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5464
1083 | Sodepur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5465
1084 | Sodepur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5466
1085 | Sodepur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5467
1086 | Sodepur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5468
1087 | Sodepur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5469
1088 | Sodepur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5470
1089 | Sodepur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5471
1090 | Sodepur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5472
1091 | Sodepur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5473
1092 | Bhatpara | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 466
1093 | Bhatpara | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 467
1094 | Bhatpara | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 468
1095 | Bhatpara | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 469
1096 | Bhatpara | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 470
1097 | Bhatpara | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 471
1098 | Bhatpara | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 472
1099 | Bhatpara | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 473
1100 | Bhatpara | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 474
1101 | Bhatpara | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 475
1102 | Bhatpara | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 476
1103 | Bhatpara | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 477
1104 | Bhatpara | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 478
1105 | Bhatpara | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 479
1106 | Bhatpara | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10030
1107 | Bhatpara | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10030
1108 | Bhatpara | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1109 | Bhatpara | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1110 | Bhatpara | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13092
1111 | Bhatpara | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5474
1112 | Bhatpara | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5475
1113 | Bhatpara | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5476
1114 | Bhatpara | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5477
1115 | Bhatpara | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5478
1116 | Bhatpara | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5479
1117 | Bhatpara | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5480
1118 | Bhatpara | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5481
1119 | Bhatpara | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5482
1120 | Bhatpara | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5483
1121 | Bhatpara | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5484
1122 | Bhatpara | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5485
1123 | Bhatpara | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5486
1124 | Bhatpara | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5487
1125 | Bhatpara | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5488
1126 | Bhatpara | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5489
1127 | Bhatpara | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5490
1128 | 10MVA PTR(Future) | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 480
1129 | 10MVA PTR(Future) | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 481
1130 | 10MVA PTR(Future) | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 482
1131 | 10MVA PTR(Future) | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 483
1132 | 10MVA PTR(Future) | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 484
1133 | 10MVA PTR(Future) | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 485
1134 | 10MVA PTR(Future) | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 486
1135 | 10MVA PTR(Future) | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 487
1136 | 10MVA PTR(Future) | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 488
1137 | 10MVA PTR(Future) | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 489
1138 | 10MVA PTR(Future) | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 490
1139 | 10MVA PTR(Future) | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 491
1140 | 10MVA PTR(Future) | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 492
1141 | 10MVA PTR(Future) | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 493
1142 | 10MVA PTR(Future) | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 494
1143 | 10MVA PTR(Future) | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 495
1144 | 10MVA PTR(Future) | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 496
1145 | 10MVA PTR(Future) | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 497
1146 | 10MVA PTR(Future) | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 498
1147 | 10MVA PTR(Future) | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 499
1148 | 10MVA PTR(Future) | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 500
1149 | 10MVA PTR(Future) | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 501
1150 | 10MVA PTR(Future) | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 502
1151 | 10MVA PTR(Future) | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 503
1152 | 10MVA PTR(Future) | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13093
1153 | 10MVA PTR(Future) | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13094
1154 | 10MVA PTR(Future) | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13095
1155 | 10MVA PTR(Future) | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13096
1156 | 10MVA PTR(Future) | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10031
1157 | 10MVA PTR(Future) | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10031
1158 | 10MVA PTR(Future) | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5491
1159 | 10MVA PTR(Future) | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5492
1160 | 10MVA PTR(Future) | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5493
1161 | 10MVA PTR(Future) | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5494
1162 | 10MVA PTR(Future) | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5495
1163 | 10MVA PTR(Future) | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5496
1164 | 10MVA PTR(Future) | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5497
1165 | 10MVA PTR(Future) | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5498
1166 | 10MVA PTR(Future) | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5499
1167 | 10MVA PTR(Future) | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5500
1168 | 10MVA PTR(Future) | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5501
1169 | 10MVA PTR(Future) | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5502
1170 | 10MVA PTR(Future) | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5503
1171 | 10MVA PTR(Future) | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5504
1172 | 10MVA PTR(Future) | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5505
1173 | 10MVA PTR(Future) | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5506
1174 | 10MVA PTR(Future) | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5507
1175 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 504
1176 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 505
1177 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 506 |  |  |  | AC CMR to be used
1178 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 507
1179 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 508
1180 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 509
1181 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 510
1182 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 511
1183 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13097
1184 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13098
1185 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5508
1186 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5509
1187 | 10MVA PTR(Future) (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5510
1188 | Spare (Future) | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 512
1189 | Spare (Future) | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 513
1190 | Spare (Future) | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 514
1191 | Spare (Future) | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 515
1192 | Spare (Future) | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 516
1193 | Spare (Future) | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 517
1194 | Spare (Future) | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 518
1195 | Spare (Future) | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 519
1196 | Spare (Future) | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 520
1197 | Spare (Future) | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 521
1198 | Spare (Future) | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 522
1199 | Spare (Future) | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 523
1200 | Spare (Future) | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13099
1201 | Spare (Future) | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13100
1202 | Spare (Future) | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13101
1203 | Spare (Future) | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10032
1204 | Spare (Future) | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10032
1205 | Spare (Future) | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5511
1206 | Spare (Future) | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5512
1207 | Spare (Future) | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5513
1208 | Spare (Future) | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5514
1209 | Spare (Future) | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5515
1210 | Spare (Future) | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5516
1211 | Spare (Future) | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5517
1212 | Spare (Future) | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5518
1213 | Spare (Future) | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5519
1214 | Spare (Future) | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5520
1215 | Spare (Future) | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5521
1216 | Spare (Future) | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5522
1217 | Spare (Future) | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5523
1218 | Spare (Future) | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5524
1219 | Spare (Future) | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5525
1220 | Spare (Future) | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5526
1221 | Spare (Future) | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5527
1222 | Spare (Future) | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5528
1223 | Spare (Future) | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5529
1224 | Spare 1(Future) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 524
1225 | Spare 1(Future) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 525
1226 | Spare 1(Future) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 526
1227 | Spare 1(Future) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 527
1228 | Spare 1(Future) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 528
1229 | Spare 1(Future) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 529
1230 | Spare 1(Future) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 530
1231 | Spare 1(Future) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 531
1232 | Spare 1(Future) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 532
1233 | Spare 1(Future) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 533
1234 | Spare 1(Future) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 534
1235 | Spare 1(Future) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 535
1236 | Spare 1(Future) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 536
1237 | Spare 1(Future) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 537
1238 | Spare 1(Future) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10033
1239 | Spare 1(Future) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10033
1240 | Spare 1(Future) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13102
1241 | Spare 1(Future) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13103
1242 | Spare 1(Future) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13104
1243 | Spare 1(Future) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5530
1244 | Spare 1(Future) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5531
1245 | Spare 1(Future) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5532
1246 | Spare 1(Future) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5533
1247 | Spare 1(Future) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5534
1248 | Spare 1(Future) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5535
1249 | Spare 1(Future) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5536
1250 | Spare 1(Future) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5537
1251 | Spare 1(Future) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5538
1252 | Spare 1(Future) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5539
1253 | Spare 1(Future) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5540
1254 | Spare 1(Future) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5541
1255 | Spare 1(Future) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5542
1256 | Spare 1(Future) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5543
1257 | Spare 1(Future) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5544
1258 | Spare 1(Future) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5545
1259 | Spare 1(Future) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5546
1260 | Spare 2(Future) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 538
1261 | Spare 2(Future) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 539
1262 | Spare 2(Future) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 540
1263 | Spare 2(Future) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 541
1264 | Spare 2(Future) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 542
1265 | Spare 2(Future) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 543
1266 | Spare 2(Future) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 544
1267 | Spare 2(Future) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 545
1268 | Spare 2(Future) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 546
1269 | Spare 2(Future) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 547
1270 | Spare 2(Future) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 548
1271 | Spare 2(Future) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 549
1272 | Spare 2(Future) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 550
1273 | Spare 2(Future) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 551
1274 | Spare 2(Future) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10034
1275 | Spare 2(Future) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10034
1276 | Spare 2(Future) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13105
1277 | Spare 2(Future) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13106
1278 | Spare 2(Future) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13107
1279 | Spare 2(Future) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5547
1280 | Spare 2(Future) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5548
1281 | Spare 2(Future) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5549
1282 | Spare 2(Future) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5550
1283 | Spare 2(Future) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5551
1284 | Spare 2(Future) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5552
1285 | Spare 2(Future) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5553
1286 | Spare 2(Future) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5554
1287 | Spare 2(Future) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5555
1288 | Spare 2(Future) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5556
1289 | Spare 2(Future) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5557
1290 | Spare 2(Future) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5558
1291 | Spare 2(Future) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5559
1292 | Spare 2(Future) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5560
1293 | Spare 2(Future) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5561
1294 | Spare 2(Future) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5562
1295 | Spare 2(Future) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5563
1296 | Spare 3(Future) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 552
1297 | Spare 3(Future) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 553
1298 | Spare 3(Future) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 554
1299 | Spare 3(Future) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 555
1300 | Spare 3(Future) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 556
1301 | Spare 3(Future) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 557
1302 | Spare 3(Future) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 558
1303 | Spare 3(Future) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 559
1304 | Spare 3(Future) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 560
1305 | Spare 3(Future) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 561
1306 | Spare 3(Future) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 562
1307 | Spare 3(Future) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 563
1308 | Spare 3(Future) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 564
1309 | Spare 3(Future) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 565
1310 | Spare 3(Future) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10035
1311 | Spare 3(Future) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10035
1312 | Spare 3(Future) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13108
1313 | Spare 3(Future) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13109
1314 | Spare 3(Future) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13110
1315 | Spare 3(Future) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5564
1316 | Spare 3(Future) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5565
1317 | Spare 3(Future) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5566
1318 | Spare 3(Future) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5567
1319 | Spare 3(Future) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5568
1320 | Spare 3(Future) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5569
1321 | Spare 3(Future) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5570
1322 | Spare 3(Future) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5571
1323 | Spare 3(Future) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5572
1324 | Spare 3(Future) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5573
1325 | Spare 3(Future) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5574
1326 | Spare 3(Future) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5575
1327 | Spare 3(Future) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5576
1328 | Spare 3(Future) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5577
1329 | Spare 3(Future) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5578
1330 | Spare 3(Future) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5579
1331 | Spare 3(Future) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5580
1332 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5581
1333 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5582
1334 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5583
1335 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5584
1336 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5585
1337 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5586
1338 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5587