## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub_Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Sub_Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Sub_Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub_Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub_Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub_Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | K.M.D.A | 33kV | I/C+Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 112
209 | K.M.D.A | 33kV | I/C+Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 113
210 | K.M.D.A | 33kV | I/C+Outgoing | Auto Trip | SPI |  |  | Soft | IED | 114
211 | K.M.D.A | 33kV | I/C+Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 115
212 | K.M.D.A | 33kV | I/C+Outgoing | Spring Charged | SPI |  |  | Soft | IED | 116
213 | K.M.D.A | 33kV | I/C+Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 117
214 | K.M.D.A | 33kV | I/C+Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 118
215 | K.M.D.A | 33kV | I/C+Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 119
216 | K.M.D.A | 33kV | I/C+Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 120
217 | K.M.D.A | 33kV | I/C+Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 121
218 | K.M.D.A | 33kV | I/C+Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 122
219 | K.M.D.A | 33kV | I/C+Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 123
220 | K.M.D.A | 33kV | I/C+Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
221 | K.M.D.A | 33kV | I/C+Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13019
222 | K.M.D.A | 33kV | I/C+Outgoing | IED RESET | SPC |  |  | Soft | IED | 13020
223 | K.M.D.A | 33kV | I/C+Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10004
224 | K.M.D.A | 33kV | I/C+Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10004
225 | K.M.D.A | 33kV | I/C+Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5068
226 | K.M.D.A | 33kV | I/C+Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5069
227 | K.M.D.A | 33kV | I/C+Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5070
228 | K.M.D.A | 33kV | I/C+Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5071
229 | K.M.D.A | 33kV | I/C+Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5072
230 | K.M.D.A | 33kV | I/C+Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5073
231 | K.M.D.A | 33kV | I/C+Outgoing | Active Power | AI |  |  | Soft | MFT | 5074
232 | K.M.D.A | 33kV | I/C+Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5075
233 | K.M.D.A | 33kV | I/C+Outgoing | Power Factor | AI |  |  | Soft | MFT | 5076
234 | K.M.D.A | 33kV | I/C+Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5077
235 | K.M.D.A | 33kV | I/C+Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5078
236 | K.M.D.A | 33kV | I/C+Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5079
237 | K.M.D.A | 33kV | I/C+Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5080
238 | K.M.D.A | 33kV | I/C+Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5081
239 | K.M.D.A | 33kV | I/C+Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5082
240 | K.M.D.A | 33kV | I/C+Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
241 | K.M.D.A | 33kV | I/C+Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
242 | K.M.D.A | 33kV | I/C+Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5085
243 | K.M.D.A | 33kV | I/C+Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5086
244 | Titagarh-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 124
245 | Titagarh-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 125
246 | Titagarh-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 126
247 | Titagarh-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 127
248 | Titagarh-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 128
249 | Titagarh-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 129
250 | Titagarh-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 130
251 | Titagarh-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 131
252 | Titagarh-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 132
253 | Titagarh-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 133
254 | Titagarh-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 134
255 | Titagarh-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 135
256 | Titagarh-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
257 | Titagarh-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13022
258 | Titagarh-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13023
259 | Titagarh-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
260 | Titagarh-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
261 | Titagarh-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5087
262 | Titagarh-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5088
263 | Titagarh-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5089
264 | Titagarh-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5090
265 | Titagarh-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5091
266 | Titagarh-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5092
267 | Titagarh-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5093
268 | Titagarh-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5094
269 | Titagarh-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5095
270 | Titagarh-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5096
271 | Titagarh-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5097
272 | Titagarh-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5098
273 | Titagarh-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5099
274 | Titagarh-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5100
275 | Titagarh-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5101
276 | Titagarh-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5102
277 | Titagarh-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5103
278 | Titagarh-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5104
279 | Titagarh-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5105
280 | Titagarh-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 136
281 | Titagarh-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 137
282 | Titagarh-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 138
283 | Titagarh-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 139
284 | Titagarh-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 140
285 | Titagarh-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 141
286 | Titagarh-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 142
287 | Titagarh-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 143
288 | Titagarh-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 144
289 | Titagarh-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 145
290 | Titagarh-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 146
291 | Titagarh-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 147
292 | Titagarh-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
293 | Titagarh-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
294 | Titagarh-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
295 | Titagarh-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
296 | Titagarh-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
297 | Titagarh-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5106
298 | Titagarh-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5107
299 | Titagarh-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5108
300 | Titagarh-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5109
301 | Titagarh-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5110
302 | Titagarh-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5111
303 | Titagarh-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5112
304 | Titagarh-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5113
305 | Titagarh-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5114
306 | Titagarh-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5115
307 | Titagarh-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5116
308 | Titagarh-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5117
309 | Titagarh-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5118
310 | Titagarh-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5119
311 | Titagarh-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5120
312 | Titagarh-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5121
313 | Titagarh-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5122
314 | Titagarh-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5123
315 | Titagarh-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5124
316 | Incomer-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 148
317 | Incomer-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 149
318 | Incomer-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 150
319 | Incomer-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 151
320 | Incomer-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 152
321 | Incomer-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 153
322 | Incomer-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 154
323 | Incomer-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 155
324 | Incomer-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 156
325 | Incomer-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 157
326 | Incomer-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 158
327 | Incomer-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 159
328 | Incomer-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 160
329 | Incomer-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
330 | Incomer-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
331 | Incomer-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
332 | Incomer-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
333 | Incomer-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13029
334 | Incomer-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5125
335 | Incomer-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5126
336 | Incomer-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5127
337 | Incomer-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5128
338 | Incomer-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5129
339 | Incomer-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5130
340 | Incomer-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5131
341 | Incomer-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5132
342 | Incomer-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5133
343 | Incomer-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5134
344 | Incomer-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5135
345 | Incomer-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5136
346 | Incomer-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5137
347 | Incomer-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5138
348 | Incomer-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5139
349 | Incomer-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5140
350 | Incomer-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5141
351 | Surendranath college | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 161
352 | Surendranath college | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 162
353 | Surendranath college | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 163
354 | Surendranath college | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 164
355 | Surendranath college | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 165
356 | Surendranath college | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 166
357 | Surendranath college | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 167
358 | Surendranath college | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 168
359 | Surendranath college | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 169
360 | Surendranath college | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 170
361 | Surendranath college | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 171
362 | Surendranath college | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 172
363 | Surendranath college | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 173
364 | Surendranath college | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 174
365 | Surendranath college | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
366 | Surendranath college | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
367 | Surendranath college | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
368 | Surendranath college | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
369 | Surendranath college | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13032
370 | Surendranath college | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5142
371 | Surendranath college | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5143
372 | Surendranath college | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5144
373 | Surendranath college | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5145
374 | Surendranath college | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5146
375 | Surendranath college | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5147
376 | Surendranath college | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5148
377 | Surendranath college | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5149
378 | Surendranath college | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5150
379 | Surendranath college | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5151
380 | Surendranath college | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5152
381 | Surendranath college | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5153
382 | Surendranath college | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5154
383 | Surendranath college | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5155
384 | Surendranath college | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5156
385 | Surendranath college | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5157
386 | Surendranath college | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5158
387 | New court | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 175
388 | New court | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 176
389 | New court | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 177
390 | New court | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 178
391 | New court | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 179
392 | New court | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 180
393 | New court | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 181
394 | New court | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 182
395 | New court | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 183
396 | New court | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 184
397 | New court | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 185
398 | New court | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 186
399 | New court | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 187
400 | New court | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 188
401 | New court | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
402 | New court | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
403 | New court | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
404 | New court | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
405 | New court | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13035
406 | New court | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5159
407 | New court | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5160
408 | New court | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5161
409 | New court | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5162
410 | New court | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5163
411 | New court | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5164
412 | New court | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5165
413 | New court | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5166
414 | New court | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5167
415 | New court | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5168
416 | New court | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5169
417 | New court | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5170
418 | New court | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5171
419 | New court | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5172
420 | New court | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5173
421 | New court | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5174
422 | New court | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5175
423 | PT.C | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 189
424 | PT.C | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 190
425 | PT.C | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 191
426 | PT.C | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 192
427 | PT.C | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 193
428 | PT.C | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 194
429 | PT.C | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 195
430 | PT.C | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 196
431 | PT.C | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 197
432 | PT.C | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 198
433 | PT.C | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 199
434 | PT.C | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 200
435 | PT.C | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 201
436 | PT.C | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 202
437 | PT.C | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
438 | PT.C | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
439 | PT.C | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
440 | PT.C | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
441 | PT.C | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
442 | PT.C | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5176
443 | PT.C | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5177
444 | PT.C | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5178
445 | PT.C | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5179
446 | PT.C | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5180
447 | PT.C | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5181
448 | PT.C | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5182
449 | PT.C | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5183
450 | PT.C | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5184
451 | PT.C | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5185
452 | PT.C | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5186
453 | PT.C | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5187
454 | PT.C | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5188
455 | PT.C | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5189
456 | PT.C | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5190
457 | PT.C | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5191
458 | PT.C | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5192
459 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 203
460 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 204
461 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 205
462 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 206
463 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 207
464 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 208
465 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 209
466 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 210 |  |  |  | AC CMR to be used
467 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 211
468 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 212
469 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10011
470 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10011
471 | Bishalaxmitala | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 213
472 | Bishalaxmitala | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 214
473 | Bishalaxmitala | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 215
474 | Bishalaxmitala | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 216
475 | Bishalaxmitala | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 217
476 | Bishalaxmitala | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 218
477 | Bishalaxmitala | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 219
478 | Bishalaxmitala | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 220
479 | Bishalaxmitala | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 221
480 | Bishalaxmitala | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 222
481 | Bishalaxmitala | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 223
482 | Bishalaxmitala | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 224
483 | Bishalaxmitala | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 225
484 | Bishalaxmitala | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 226
485 | Bishalaxmitala | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
486 | Bishalaxmitala | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
487 | Bishalaxmitala | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
488 | Bishalaxmitala | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
489 | Bishalaxmitala | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
490 | Bishalaxmitala | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5193
491 | Bishalaxmitala | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5194
492 | Bishalaxmitala | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5195
493 | Bishalaxmitala | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5196
494 | Bishalaxmitala | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5197
495 | Bishalaxmitala | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5198
496 | Bishalaxmitala | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5199
497 | Bishalaxmitala | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5200
498 | Bishalaxmitala | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5201
499 | Bishalaxmitala | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5202
500 | Bishalaxmitala | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5203
501 | Bishalaxmitala | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5204
502 | Bishalaxmitala | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5205
503 | Bishalaxmitala | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5206
504 | Bishalaxmitala | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5207
505 | Bishalaxmitala | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5208
506 | Bishalaxmitala | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5209
507 | Fishery gate | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 227
508 | Fishery gate | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 228
509 | Fishery gate | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 229
510 | Fishery gate | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 230
511 | Fishery gate | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 231
512 | Fishery gate | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 232
513 | Fishery gate | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 233
514 | Fishery gate | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 234
515 | Fishery gate | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 235
516 | Fishery gate | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 236
517 | Fishery gate | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 237
518 | Fishery gate | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 238
519 | Fishery gate | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 239
520 | Fishery gate | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 240
521 | Fishery gate | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
522 | Fishery gate | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
523 | Fishery gate | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
524 | Fishery gate | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
525 | Fishery gate | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
526 | Fishery gate | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5210
527 | Fishery gate | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5211
528 | Fishery gate | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5212
529 | Fishery gate | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5213
530 | Fishery gate | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5214
531 | Fishery gate | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5215
532 | Fishery gate | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5216
533 | Fishery gate | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5217
534 | Fishery gate | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5218
535 | Fishery gate | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5219
536 | Fishery gate | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5220
537 | Fishery gate | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5221
538 | Fishery gate | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5222
539 | Fishery gate | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5223
540 | Fishery gate | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5224
541 | Fishery gate | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5225
542 | Fishery gate | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5226
543 | Lalkuthi | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 241
544 | Lalkuthi | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 242
545 | Lalkuthi | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 243
546 | Lalkuthi | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 244
547 | Lalkuthi | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 245
548 | Lalkuthi | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 246
549 | Lalkuthi | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 247
550 | Lalkuthi | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 248
551 | Lalkuthi | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 249
552 | Lalkuthi | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 250
553 | Lalkuthi | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 251
554 | Lalkuthi | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 252
555 | Lalkuthi | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 253
556 | Lalkuthi | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 254
557 | Lalkuthi | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
558 | Lalkuthi | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
559 | Lalkuthi | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
560 | Lalkuthi | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
561 | Lalkuthi | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
562 | Lalkuthi | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5227
563 | Lalkuthi | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5228
564 | Lalkuthi | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5229
565 | Lalkuthi | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5230
566 | Lalkuthi | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5231
567 | Lalkuthi | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5232
568 | Lalkuthi | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5233
569 | Lalkuthi | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5234
570 | Lalkuthi | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5235
571 | Lalkuthi | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5236
572 | Lalkuthi | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5237
573 | Lalkuthi | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5238
574 | Lalkuthi | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5239
575 | Lalkuthi | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5240
576 | Lalkuthi | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5241
577 | Lalkuthi | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5242
578 | Lalkuthi | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5243
579 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 255
580 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 256
581 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 257
582 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 258
583 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 259
584 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 260
585 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 261
586 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 262
587 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 263
588 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 264
589 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 265
590 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 266
591 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 267
592 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
593 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
594 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
595 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13049
596 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13050
597 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5244
598 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5245
599 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5246
600 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5247
601 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5248
602 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5249
603 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5250
604 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5251
605 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5252
606 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5253
607 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5254
608 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5255
609 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5256
610 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5257
611 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5258
612 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5259
613 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5260
614 | Bus coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 268
615 | Bus coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 269
616 | Bus coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 270
617 | Bus coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 271
618 | Bus coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 272
619 | Bus coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 273
620 | Bus coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 274
621 | Bus coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 275 |  |  |  | AC CMR to be used
622 | Bus coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 276
623 | Bus coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 277
624 | Bus coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10016
625 | Bus coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10016
626 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 278
627 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 279
628 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 280
629 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 281
630 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 282
631 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 283
632 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 284
633 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 285
634 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 286
635 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 287
636 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 288
637 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 289
638 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 290
639 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
640 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
641 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
642 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13052
643 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13053
644 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5261
645 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5262
646 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5263
647 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5264
648 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5265
649 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5266
650 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5267
651 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5268
652 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5269
653 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5270
654 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5271
655 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5272
656 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5273
657 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5274
658 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5275
659 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5276
660 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5277
661 | Barrack pore | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 291
662 | Barrack pore | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 292
663 | Barrack pore | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 293
664 | Barrack pore | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 294
665 | Barrack pore | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 295
666 | Barrack pore | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 296
667 | Barrack pore | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 297
668 | Barrack pore | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 298
669 | Barrack pore | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 299
670 | Barrack pore | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 300
671 | Barrack pore | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 301
672 | Barrack pore | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 302
673 | Barrack pore | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 303
674 | Barrack pore | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 304
675 | Barrack pore | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
676 | Barrack pore | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
677 | Barrack pore | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
678 | Barrack pore | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
679 | Barrack pore | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
680 | Barrack pore | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5278
681 | Barrack pore | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5279
682 | Barrack pore | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5280
683 | Barrack pore | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5281
684 | Barrack pore | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5282
685 | Barrack pore | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5283
686 | Barrack pore | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5284
687 | Barrack pore | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5285
688 | Barrack pore | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5286
689 | Barrack pore | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5287
690 | Barrack pore | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5288
691 | Barrack pore | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5289
692 | Barrack pore | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5290
693 | Barrack pore | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5291
694 | Barrack pore | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5292
695 | Barrack pore | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5293
696 | Barrack pore | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5294
697 | Ghoratala | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 305
698 | Ghoratala | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 306
699 | Ghoratala | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 307
700 | Ghoratala | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 308
701 | Ghoratala | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 309
702 | Ghoratala | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 310
703 | Ghoratala | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 311
704 | Ghoratala | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 312
705 | Ghoratala | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 313
706 | Ghoratala | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 314
707 | Ghoratala | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 315
708 | Ghoratala | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 316
709 | Ghoratala | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 317
710 | Ghoratala | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 318
711 | Ghoratala | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
712 | Ghoratala | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
713 | Ghoratala | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
714 | Ghoratala | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
715 | Ghoratala | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
716 | Ghoratala | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5295
717 | Ghoratala | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5296
718 | Ghoratala | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5297
719 | Ghoratala | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5298
720 | Ghoratala | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5299
721 | Ghoratala | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5300
722 | Ghoratala | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5301
723 | Ghoratala | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5302
724 | Ghoratala | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5303
725 | Ghoratala | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5304
726 | Ghoratala | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5305
727 | Ghoratala | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5306
728 | Ghoratala | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5307
729 | Ghoratala | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5308
730 | Ghoratala | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5309
731 | Ghoratala | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5310
732 | Ghoratala | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5311
733 | Sukanta sadan | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 319
734 | Sukanta sadan | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 320
735 | Sukanta sadan | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 321
736 | Sukanta sadan | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 322
737 | Sukanta sadan | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 323
738 | Sukanta sadan | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 324
739 | Sukanta sadan | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 325
740 | Sukanta sadan | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 326
741 | Sukanta sadan | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 327
742 | Sukanta sadan | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 328
743 | Sukanta sadan | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 329
744 | Sukanta sadan | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 330
745 | Sukanta sadan | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 331
746 | Sukanta sadan | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 332
747 | Sukanta sadan | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
748 | Sukanta sadan | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
749 | Sukanta sadan | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
750 | Sukanta sadan | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
751 | Sukanta sadan | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
752 | Sukanta sadan | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5312
753 | Sukanta sadan | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5313
754 | Sukanta sadan | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5314
755 | Sukanta sadan | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5315
756 | Sukanta sadan | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5316
757 | Sukanta sadan | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5317
758 | Sukanta sadan | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5318
759 | Sukanta sadan | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5319
760 | Sukanta sadan | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5320
761 | Sukanta sadan | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5321
762 | Sukanta sadan | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5322
763 | Sukanta sadan | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5323
764 | Sukanta sadan | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5324
765 | Sukanta sadan | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5325
766 | Sukanta sadan | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5326
767 | Sukanta sadan | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5327
768 | Sukanta sadan | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5328
769 | Maniram pur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 333
770 | Maniram pur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 334
771 | Maniram pur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 335
772 | Maniram pur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 336
773 | Maniram pur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 337
774 | Maniram pur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 338
775 | Maniram pur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 339
776 | Maniram pur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 340
777 | Maniram pur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 341
778 | Maniram pur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 342
779 | Maniram pur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 343
780 | Maniram pur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 344
781 | Maniram pur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 345
782 | Maniram pur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 346
783 | Maniram pur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
784 | Maniram pur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
785 | Maniram pur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
786 | Maniram pur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
787 | Maniram pur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
788 | Maniram pur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5329
789 | Maniram pur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5330
790 | Maniram pur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5331
791 | Maniram pur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5332
792 | Maniram pur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5333
793 | Maniram pur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5334
794 | Maniram pur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5335
795 | Maniram pur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5336
796 | Maniram pur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5337
797 | Maniram pur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5338
798 | Maniram pur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5339
799 | Maniram pur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5340
800 | Maniram pur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5341
801 | Maniram pur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5342
802 | Maniram pur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5343
803 | Maniram pur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5344
804 | Maniram pur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5345
805 | Shantasri pally | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 347
806 | Shantasri pally | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 348
807 | Shantasri pally | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 349
808 | Shantasri pally | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 350
809 | Shantasri pally | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 351
810 | Shantasri pally | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 352
811 | Shantasri pally | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 353
812 | Shantasri pally | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 354
813 | Shantasri pally | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 355
814 | Shantasri pally | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 356
815 | Shantasri pally | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 357
816 | Shantasri pally | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 358
817 | Shantasri pally | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 359
818 | Shantasri pally | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 360
819 | Shantasri pally | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
820 | Shantasri pally | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
821 | Shantasri pally | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
822 | Shantasri pally | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
823 | Shantasri pally | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
824 | Shantasri pally | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5346
825 | Shantasri pally | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5347
826 | Shantasri pally | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5348
827 | Shantasri pally | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5349
828 | Shantasri pally | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5350
829 | Shantasri pally | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5351
830 | Shantasri pally | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5352
831 | Shantasri pally | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5353
832 | Shantasri pally | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5354
833 | Shantasri pally | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5355
834 | Shantasri pally | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5356
835 | Shantasri pally | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5357
836 | Shantasri pally | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5358
837 | Shantasri pally | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5359
838 | Shantasri pally | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5360
839 | Shantasri pally | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5361
840 | Shantasri pally | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5362
841 | Spare 33kV (Future) | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 361
842 | Spare 33kV (Future) | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 362
843 | Spare 33kV (Future) | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 363
844 | Spare 33kV (Future) | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 364
845 | Spare 33kV (Future) | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 365
846 | Spare 33kV (Future) | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 366
847 | Spare 33kV (Future) | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 367
848 | Spare 33kV (Future) | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 368
849 | Spare 33kV (Future) | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 369
850 | Spare 33kV (Future) | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 370
851 | Spare 33kV (Future) | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 371
852 | Spare 33kV (Future) | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 372
853 | Spare 33kV (Future) | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
854 | Spare 33kV (Future) | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
855 | Spare 33kV (Future) | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13071
856 | Spare 33kV (Future) | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
857 | Spare 33kV (Future) | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
858 | Spare 33kV (Future) | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5363
859 | Spare 33kV (Future) | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5364
860 | Spare 33kV (Future) | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5365
861 | Spare 33kV (Future) | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5366
862 | Spare 33kV (Future) | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5367
863 | Spare 33kV (Future) | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5368
864 | Spare 33kV (Future) | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5369
865 | Spare 33kV (Future) | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5370
866 | Spare 33kV (Future) | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5371
867 | Spare 33kV (Future) | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5372
868 | Spare 33kV (Future) | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5373
869 | Spare 33kV (Future) | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5374
870 | Spare 33kV (Future) | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5375
871 | Spare 33kV (Future) | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5376
872 | Spare 33kV (Future) | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5377
873 | Spare 33kV (Future) | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5378
874 | Spare 33kV (Future) | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5379
875 | Spare 33kV (Future) | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5380
876 | Spare 33kV (Future) | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5381
877 | Spare 1(Future) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 373
878 | Spare 1(Future) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 374
879 | Spare 1(Future) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 375
880 | Spare 1(Future) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 376
881 | Spare 1(Future) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 377
882 | Spare 1(Future) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 378
883 | Spare 1(Future) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 379
884 | Spare 1(Future) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 380
885 | Spare 1(Future) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 381
886 | Spare 1(Future) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 382
887 | Spare 1(Future) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 383
888 | Spare 1(Future) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 384
889 | Spare 1(Future) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 385
890 | Spare 1(Future) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 386
891 | Spare 1(Future) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
892 | Spare 1(Future) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
893 | Spare 1(Future) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
894 | Spare 1(Future) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
895 | Spare 1(Future) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
896 | Spare 1(Future) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5382
897 | Spare 1(Future) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5383
898 | Spare 1(Future) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5384
899 | Spare 1(Future) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5385
900 | Spare 1(Future) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5386
901 | Spare 1(Future) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5387
902 | Spare 1(Future) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5388
903 | Spare 1(Future) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5389
904 | Spare 1(Future) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5390
905 | Spare 1(Future) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5391
906 | Spare 1(Future) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5392
907 | Spare 1(Future) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5393
908 | Spare 1(Future) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5394
909 | Spare 1(Future) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5395
910 | Spare 1(Future) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5396
911 | Spare 1(Future) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5397
912 | Spare 1(Future) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5398
913 | Spare 2(Future) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 387
914 | Spare 2(Future) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 388
915 | Spare 2(Future) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 389
916 | Spare 2(Future) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 390
917 | Spare 2(Future) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 391
918 | Spare 2(Future) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 392
919 | Spare 2(Future) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 393
920 | Spare 2(Future) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 394
921 | Spare 2(Future) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 395
922 | Spare 2(Future) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 396
923 | Spare 2(Future) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 397
924 | Spare 2(Future) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 398
925 | Spare 2(Future) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 399
926 | Spare 2(Future) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 400
927 | Spare 2(Future) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10025
928 | Spare 2(Future) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10025
929 | Spare 2(Future) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
930 | Spare 2(Future) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13076
931 | Spare 2(Future) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13077
932 | Spare 2(Future) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5399
933 | Spare 2(Future) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5400
934 | Spare 2(Future) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5401
935 | Spare 2(Future) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5402
936 | Spare 2(Future) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5403
937 | Spare 2(Future) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5404
938 | Spare 2(Future) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5405
939 | Spare 2(Future) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5406
940 | Spare 2(Future) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5407
941 | Spare 2(Future) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5408
942 | Spare 2(Future) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5409
943 | Spare 2(Future) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5410
944 | Spare 2(Future) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5411
945 | Spare 2(Future) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5412
946 | Spare 2(Future) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5413
947 | Spare 2(Future) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5414
948 | Spare 2(Future) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5415
949 | Spare 3(Future) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 401
950 | Spare 3(Future) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 402
951 | Spare 3(Future) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 403
952 | Spare 3(Future) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 404
953 | Spare 3(Future) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 405
954 | Spare 3(Future) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 406
955 | Spare 3(Future) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 407
956 | Spare 3(Future) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 408
957 | Spare 3(Future) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 409
958 | Spare 3(Future) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 410
959 | Spare 3(Future) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 411
960 | Spare 3(Future) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 412
961 | Spare 3(Future) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 413
962 | Spare 3(Future) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 414
963 | Spare 3(Future) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
964 | Spare 3(Future) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
965 | Spare 3(Future) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
966 | Spare 3(Future) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13079
967 | Spare 3(Future) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13080
968 | Spare 3(Future) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5416
969 | Spare 3(Future) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5417
970 | Spare 3(Future) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5418
971 | Spare 3(Future) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5419
972 | Spare 3(Future) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5420
973 | Spare 3(Future) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5421
974 | Spare 3(Future) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5422
975 | Spare 3(Future) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5423
976 | Spare 3(Future) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5424
977 | Spare 3(Future) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5425
978 | Spare 3(Future) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5426
979 | Spare 3(Future) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5427
980 | Spare 3(Future) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5428
981 | Spare 3(Future) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5429
982 | Spare 3(Future) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5430
983 | Spare 3(Future) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5431
984 | Spare 3(Future) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5432
985 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5433
986 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5434
987 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5435
988 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5436
989 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5437
990 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5438
991 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5439