## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | 30V DC-3 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
23 | 30V DC-3 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 15
24 | 30V DC-3 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 16
25 | 30V DC-3 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 17
26 | 30V DC-3 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 18
27 | 30V DC-3 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5008
28 | 30V DC-3 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5009
29 | 30V DC-3 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5010
30 | Substation Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
31 | Substation Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
32 | Substation Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
33 | Substation Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 19 |  |  |  | AC CMR to be used
34 | Substation Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 20
35 | Substation Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
36 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5011
37 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5012
38 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5013
39 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5014
40 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5015
41 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5016
42 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5017
43 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 21
44 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 22
45 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 23
46 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 24
47 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 25
48 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 26
49 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 27
50 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 28
51 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 29
52 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 30
53 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 31
54 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 32
55 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 33
56 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 34
57 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 35
58 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 36
59 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 37
60 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 38
61 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 39
62 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 40
63 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 41
64 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 42
65 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 43
66 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 44
67 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
68 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
69 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
70 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
71 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
72 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
73 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5018
74 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5019
75 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5020
76 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5021
77 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5022
78 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5023
79 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5024
80 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5025
81 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5026
82 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5027
83 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5028
84 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5029
85 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5030
86 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5031
87 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5032
88 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5033
89 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5034
90 | Transformer-1(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 45
91 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 46
92 | Transformer-1(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 47 |  |  |  | AC CMR to be used
93 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 48
94 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 49
95 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 50
96 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 51
97 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 52
98 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
99 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
100 | Transformer-1(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5035
101 | Transformer-1(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5036
102 | Transformer-1(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5037
103 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 53
104 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 54
105 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 55
106 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 56
107 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 57
108 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 58
109 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 59
110 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 60
111 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 61
112 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 62
113 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 63
114 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 64
115 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 65
116 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 66
117 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 67
118 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 68
119 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 69
120 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 70
121 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 71
122 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 72
123 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 73
124 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 74
125 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 75
126 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 76
127 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
128 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
129 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
130 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
131 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
132 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
133 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5038
134 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5039
135 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5040
136 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5041
137 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5042
138 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5043
139 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5044
140 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5045
141 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5046
142 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5047
143 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5048
144 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5049
145 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5050
146 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5051
147 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5052
148 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5053
149 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5054
150 | Transformer-2(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 77
151 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 78
152 | Transformer-2(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 79 |  |  |  | AC CMR to be used
153 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 80
154 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 81
155 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 82
156 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 83
157 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 84
158 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
159 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
160 | Transformer-2(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5055
161 | Transformer-2(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5056
162 | Transformer-2(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5057
163 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 85
164 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 86
165 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 87
166 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 88
167 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 89
168 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 90
169 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 91
170 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 92
171 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 93
172 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 94
173 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 95
174 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 96
175 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 97
176 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 98
177 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 99
178 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 100
179 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 101
180 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 102
181 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 103
182 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 104
183 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 105
184 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 106
185 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 107
186 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 108
187 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
188 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
189 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
190 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
191 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
192 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
193 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5058
194 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5059
195 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5060
196 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5061
197 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5062
198 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5063
199 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5064
200 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5065
201 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5066
202 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5067
203 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5068
204 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5069
205 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5070
206 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5071
207 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5072
208 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5073
209 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5074
210 | Transformer-3(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 109
211 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 110
212 | Transformer-3(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 111 |  |  |  | AC CMR to be used
213 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 112
214 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 113
215 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 114
216 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 115
217 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 116
218 | Transformer-3(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
219 | Transformer-3(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
220 | Transformer-3(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5075
221 | Transformer-3(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5076
222 | Transformer-3(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5077
223 | Transformer-4 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 117
224 | Transformer-4 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 118
225 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 119
226 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 120
227 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 121
228 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 122
229 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 123
230 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 124
231 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 125
232 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 126
233 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 127
234 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 128
235 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 129
236 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 130
237 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 131
238 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 132
239 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 133
240 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 134
241 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 135
242 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 136
243 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 137
244 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 138
245 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 139
246 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 140
247 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
248 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
249 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
250 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
251 | Transformer-4 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
252 | Transformer-4 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
253 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5078
254 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5079
255 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5080
256 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5081
257 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5082
258 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5083
259 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5084
260 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5085
261 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5086
262 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5087
263 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5088
264 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5089
265 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5090
266 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5091
267 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5092
268 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5093
269 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5094
270 | Transformer-4(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 141
271 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 142
272 | Transformer-4(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 143 |  |  |  | AC CMR to be used
273 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 144
274 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 145
275 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 146
276 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 147
277 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 148
278 | Transformer-4(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
279 | Transformer-4(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
280 | Transformer-4(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5095
281 | Transformer-4(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5096
282 | Transformer-4(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5097
283 | Transformer-5 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 149
284 | Transformer-5 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 150
285 | Transformer-5 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 151
286 | Transformer-5 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 152
287 | Transformer-5 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 153
288 | Transformer-5 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 154
289 | Transformer-5 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 155
290 | Transformer-5 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 156
291 | Transformer-5 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 157
292 | Transformer-5 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 158
293 | Transformer-5 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 159
294 | Transformer-5 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 160
295 | Transformer-5 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 161
296 | Transformer-5 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 162
297 | Transformer-5 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 163
298 | Transformer-5 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 164
299 | Transformer-5 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 165
300 | Transformer-5 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 166
301 | Transformer-5 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 167
302 | Transformer-5 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 168
303 | Transformer-5 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 169
304 | Transformer-5 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 170
305 | Transformer-5 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 171
306 | Transformer-5 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 172
307 | Transformer-5 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13024
308 | Transformer-5 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13025
309 | Transformer-5 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13026
310 | Transformer-5 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13027
311 | Transformer-5 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10005
312 | Transformer-5 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10005
313 | Transformer-5 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5098
314 | Transformer-5 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5099
315 | Transformer-5 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5100
316 | Transformer-5 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5101
317 | Transformer-5 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5102
318 | Transformer-5 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5103
319 | Transformer-5 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5104
320 | Transformer-5 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5105
321 | Transformer-5 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5106
322 | Transformer-5 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5107
323 | Transformer-5 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5108
324 | Transformer-5 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5109
325 | Transformer-5 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5110
326 | Transformer-5 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5111
327 | Transformer-5 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5112
328 | Transformer-5 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5113
329 | Transformer-5 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5114
330 | Transformer-5(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 173
331 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 174
332 | Transformer-5(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 175 |  |  |  | AC CMR to be used
333 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 176
334 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 177
335 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 178
336 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 179
337 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 180
338 | Transformer-5(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13028
339 | Transformer-5(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13029
340 | Transformer-5(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5115
341 | Transformer-5(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5116
342 | Transformer-5(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5117
343 | Mohispota-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 181
344 | Mohispota-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 182
345 | Mohispota-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 183
346 | Mohispota-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 184
347 | Mohispota-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 185
348 | Mohispota-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 186
349 | Mohispota-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 187
350 | Mohispota-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 188
351 | Mohispota-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 189
352 | Mohispota-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 190
353 | Mohispota-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 191
354 | Mohispota-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 192
355 | Mohispota-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
356 | Mohispota-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13031
357 | Mohispota-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13032
358 | Mohispota-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
359 | Mohispota-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
360 | Mohispota-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5118
361 | Mohispota-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5119
362 | Mohispota-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5120
363 | Mohispota-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5121
364 | Mohispota-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5122
365 | Mohispota-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5123
366 | Mohispota-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5124
367 | Mohispota-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5125
368 | Mohispota-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5126
369 | Mohispota-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5127
370 | Mohispota-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5128
371 | Mohispota-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5129
372 | Mohispota-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5130
373 | Mohispota-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5131
374 | Mohispota-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5132
375 | Mohispota-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5133
376 | Mohispota-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5134
377 | Mohispota-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5135
378 | Mohispota-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5136
379 | Texmaco-2 | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 193
380 | Texmaco-2 | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 194
381 | Texmaco-2 | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 195
382 | Texmaco-2 | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 196
383 | Texmaco-2 | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 197
384 | Texmaco-2 | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 198
385 | Texmaco-2 | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 199
386 | Texmaco-2 | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 200
387 | Texmaco-2 | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 201
388 | Texmaco-2 | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 202
389 | Texmaco-2 | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 203
390 | Texmaco-2 | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 204
391 | Texmaco-2 | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
392 | Texmaco-2 | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
393 | Texmaco-2 | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13035
394 | Texmaco-2 | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
395 | Texmaco-2 | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
396 | Texmaco-2 | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5137
397 | Texmaco-2 | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5138
398 | Texmaco-2 | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5139
399 | Texmaco-2 | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5140
400 | Texmaco-2 | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5141
401 | Texmaco-2 | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5142
402 | Texmaco-2 | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5143
403 | Texmaco-2 | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5144
404 | Texmaco-2 | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5145
405 | Texmaco-2 | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5146
406 | Texmaco-2 | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5147
407 | Texmaco-2 | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5148
408 | Texmaco-2 | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5149
409 | Texmaco-2 | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5150
410 | Texmaco-2 | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5151
411 | Texmaco-2 | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5152
412 | Texmaco-2 | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5153
413 | Texmaco-2 | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5154
414 | Texmaco-2 | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5155
415 | Agarpara CKT-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 205
416 | Agarpara CKT-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 206
417 | Agarpara CKT-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 207
418 | Agarpara CKT-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 208
419 | Agarpara CKT-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 209
420 | Agarpara CKT-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 210
421 | Agarpara CKT-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 211
422 | Agarpara CKT-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 212
423 | Agarpara CKT-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 213
424 | Agarpara CKT-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 214
425 | Agarpara CKT-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 215
426 | Agarpara CKT-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 216
427 | Agarpara CKT-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
428 | Agarpara CKT-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
429 | Agarpara CKT-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13038
430 | Agarpara CKT-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
431 | Agarpara CKT-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
432 | Agarpara CKT-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5156
433 | Agarpara CKT-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5157
434 | Agarpara CKT-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5158
435 | Agarpara CKT-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5159
436 | Agarpara CKT-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5160
437 | Agarpara CKT-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5161
438 | Agarpara CKT-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5162
439 | Agarpara CKT-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5163
440 | Agarpara CKT-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5164
441 | Agarpara CKT-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5165
442 | Agarpara CKT-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5166
443 | Agarpara CKT-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5167
444 | Agarpara CKT-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5168
445 | Agarpara CKT-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5169
446 | Agarpara CKT-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5170
447 | Agarpara CKT-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5171
448 | Agarpara CKT-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5172
449 | Agarpara CKT-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5173
450 | Agarpara CKT-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5174
451 | Mohispota-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 217
452 | Mohispota-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 218
453 | Mohispota-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 219
454 | Mohispota-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 220
455 | Mohispota-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 221
456 | Mohispota-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 222
457 | Mohispota-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 223
458 | Mohispota-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 224
459 | Mohispota-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 225
460 | Mohispota-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 226
461 | Mohispota-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 227
462 | Mohispota-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 228
463 | Mohispota-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
464 | Mohispota-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13040
465 | Mohispota-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13041
466 | Mohispota-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
467 | Mohispota-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
468 | Mohispota-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5175
469 | Mohispota-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5176
470 | Mohispota-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5177
471 | Mohispota-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5178
472 | Mohispota-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5179
473 | Mohispota-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5180
474 | Mohispota-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5181
475 | Mohispota-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5182
476 | Mohispota-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5183
477 | Mohispota-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5184
478 | Mohispota-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5185
479 | Mohispota-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5186
480 | Mohispota-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5187
481 | Mohispota-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5188
482 | Mohispota-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5189
483 | Mohispota-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5190
484 | Mohispota-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5191
485 | Mohispota-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5192
486 | Mohispota-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5193
487 | Agarpara CKT-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 229
488 | Agarpara CKT-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 230
489 | Agarpara CKT-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 231
490 | Agarpara CKT-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 232
491 | Agarpara CKT-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 233
492 | Agarpara CKT-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 234
493 | Agarpara CKT-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 235
494 | Agarpara CKT-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 236
495 | Agarpara CKT-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 237
496 | Agarpara CKT-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 238
497 | Agarpara CKT-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 239
498 | Agarpara CKT-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 240
499 | Agarpara CKT-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
500 | Agarpara CKT-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13043
501 | Agarpara CKT-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13044
502 | Agarpara CKT-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
503 | Agarpara CKT-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
504 | Agarpara CKT-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5194
505 | Agarpara CKT-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5195
506 | Agarpara CKT-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5196
507 | Agarpara CKT-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5197
508 | Agarpara CKT-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5198
509 | Agarpara CKT-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5199
510 | Agarpara CKT-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5200
511 | Agarpara CKT-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5201
512 | Agarpara CKT-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5202
513 | Agarpara CKT-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5203
514 | Agarpara CKT-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5204
515 | Agarpara CKT-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5205
516 | Agarpara CKT-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5206
517 | Agarpara CKT-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5207
518 | Agarpara CKT-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5208
519 | Agarpara CKT-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5209
520 | Agarpara CKT-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5210
521 | Agarpara CKT-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5211
522 | Agarpara CKT-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5212
523 | Texmaco-1 | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 241
524 | Texmaco-1 | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 242
525 | Texmaco-1 | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 243
526 | Texmaco-1 | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 244
527 | Texmaco-1 | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 245
528 | Texmaco-1 | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 246
529 | Texmaco-1 | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 247
530 | Texmaco-1 | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 248
531 | Texmaco-1 | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 249
532 | Texmaco-1 | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 250
533 | Texmaco-1 | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 251
534 | Texmaco-1 | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 252
535 | Texmaco-1 | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
536 | Texmaco-1 | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
537 | Texmaco-1 | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13047
538 | Texmaco-1 | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
539 | Texmaco-1 | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
540 | Texmaco-1 | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5213
541 | Texmaco-1 | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5214
542 | Texmaco-1 | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5215
543 | Texmaco-1 | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5216
544 | Texmaco-1 | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5217
545 | Texmaco-1 | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5218
546 | Texmaco-1 | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5219
547 | Texmaco-1 | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5220
548 | Texmaco-1 | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5221
549 | Texmaco-1 | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5222
550 | Texmaco-1 | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5223
551 | Texmaco-1 | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5224
552 | Texmaco-1 | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5225
553 | Texmaco-1 | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5226
554 | Texmaco-1 | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5227
555 | Texmaco-1 | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5228
556 | Texmaco-1 | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5229
557 | Texmaco-1 | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5230
558 | Texmaco-1 | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5231
559 | Spare-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 253
560 | Spare-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 254
561 | Spare-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 255
562 | Spare-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 256
563 | Spare-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 257
564 | Spare-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 258
565 | Spare-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 259
566 | Spare-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 260
567 | Spare-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 261
568 | Spare-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 262
569 | Spare-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 263
570 | Spare-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 264
571 | Spare-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 265
572 | Spare-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 266
573 | Spare-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
574 | Spare-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
575 | Spare-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
576 | Spare-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
577 | Spare-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
578 | Spare-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5232
579 | Spare-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5233
580 | Spare-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5234
581 | Spare-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5235
582 | Spare-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5236
583 | Spare-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5237
584 | Spare-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5238
585 | Spare-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5239
586 | Spare-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5240
587 | Spare-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5241
588 | Spare-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5242
589 | Spare-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5243
590 | Spare-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5244
591 | Spare-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5245
592 | Spare-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5246
593 | Spare-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5247
594 | Spare-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5248
595 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 267
596 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 268
597 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 269
598 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 270
599 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 271
600 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 272
601 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 273
602 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 274
603 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 275
604 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 276
605 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 277
606 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 278
607 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 279
608 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
609 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
610 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
611 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13052
612 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13053
613 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5249
614 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5250
615 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5251
616 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5252
617 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5253
618 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5254
619 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5255
620 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5256
621 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5257
622 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5258
623 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5259
624 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5260
625 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5261
626 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5262
627 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5263
628 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5264
629 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5265
630 | Ajadhind Nagar | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 280
631 | Ajadhind Nagar | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 281
632 | Ajadhind Nagar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 282
633 | Ajadhind Nagar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 283
634 | Ajadhind Nagar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 284
635 | Ajadhind Nagar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 285
636 | Ajadhind Nagar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 286
637 | Ajadhind Nagar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 287
638 | Ajadhind Nagar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 288
639 | Ajadhind Nagar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 289
640 | Ajadhind Nagar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 290
641 | Ajadhind Nagar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 291
642 | Ajadhind Nagar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 292
643 | Ajadhind Nagar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 293
644 | Ajadhind Nagar | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
645 | Ajadhind Nagar | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
646 | Ajadhind Nagar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
647 | Ajadhind Nagar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
648 | Ajadhind Nagar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
649 | Ajadhind Nagar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5266
650 | Ajadhind Nagar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5267
651 | Ajadhind Nagar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5268
652 | Ajadhind Nagar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5269
653 | Ajadhind Nagar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5270
654 | Ajadhind Nagar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5271
655 | Ajadhind Nagar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5272
656 | Ajadhind Nagar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5273
657 | Ajadhind Nagar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5274
658 | Ajadhind Nagar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5275
659 | Ajadhind Nagar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5276
660 | Ajadhind Nagar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5277
661 | Ajadhind Nagar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5278
662 | Ajadhind Nagar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5279
663 | Ajadhind Nagar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5280
664 | Ajadhind Nagar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5281
665 | Ajadhind Nagar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5282
666 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 294
667 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 295
668 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 296
669 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 297
670 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 298
671 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 299
672 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 300
673 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 301 |  |  |  | AC CMR to be used
674 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 302
675 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 303
676 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10015
677 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10015
678 | Chowdhury Para | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 304
679 | Chowdhury Para | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 305
680 | Chowdhury Para | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 306
681 | Chowdhury Para | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 307
682 | Chowdhury Para | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 308
683 | Chowdhury Para | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 309
684 | Chowdhury Para | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 310
685 | Chowdhury Para | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 311
686 | Chowdhury Para | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 312
687 | Chowdhury Para | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 313
688 | Chowdhury Para | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 314
689 | Chowdhury Para | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 315
690 | Chowdhury Para | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 316
691 | Chowdhury Para | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 317
692 | Chowdhury Para | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
693 | Chowdhury Para | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
694 | Chowdhury Para | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
695 | Chowdhury Para | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
696 | Chowdhury Para | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
697 | Chowdhury Para | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5283
698 | Chowdhury Para | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5284
699 | Chowdhury Para | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5285
700 | Chowdhury Para | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5286
701 | Chowdhury Para | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5287
702 | Chowdhury Para | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5288
703 | Chowdhury Para | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5289
704 | Chowdhury Para | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5290
705 | Chowdhury Para | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5291
706 | Chowdhury Para | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5292
707 | Chowdhury Para | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5293
708 | Chowdhury Para | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5294
709 | Chowdhury Para | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5295
710 | Chowdhury Para | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5296
711 | Chowdhury Para | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5297
712 | Chowdhury Para | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5298
713 | Chowdhury Para | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5299
714 | Pike Para | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 318
715 | Pike Para | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 319
716 | Pike Para | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 320
717 | Pike Para | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 321
718 | Pike Para | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 322
719 | Pike Para | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 323
720 | Pike Para | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 324
721 | Pike Para | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 325
722 | Pike Para | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 326
723 | Pike Para | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 327
724 | Pike Para | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 328
725 | Pike Para | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 329
726 | Pike Para | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 330
727 | Pike Para | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 331
728 | Pike Para | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
729 | Pike Para | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
730 | Pike Para | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
731 | Pike Para | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
732 | Pike Para | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
733 | Pike Para | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5300
734 | Pike Para | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5301
735 | Pike Para | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5302
736 | Pike Para | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5303
737 | Pike Para | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5304
738 | Pike Para | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5305
739 | Pike Para | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5306
740 | Pike Para | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5307
741 | Pike Para | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5308
742 | Pike Para | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5309
743 | Pike Para | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5310
744 | Pike Para | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5311
745 | Pike Para | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5312
746 | Pike Para | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5313
747 | Pike Para | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5314
748 | Pike Para | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5315
749 | Pike Para | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5316
750 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 332
751 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 333
752 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 334
753 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 335
754 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 336
755 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 337
756 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 338
757 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 339
758 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 340
759 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 341
760 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 342
761 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 343
762 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 344
763 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
764 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
765 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
766 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13064
767 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13065
768 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5317
769 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5318
770 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5319
771 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5320
772 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5321
773 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5322
774 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5323
775 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5324
776 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5325
777 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5326
778 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5327
779 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5328
780 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5329
781 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5330
782 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5331
783 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5332
784 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5333
785 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 345
786 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 346
787 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 347
788 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 348
789 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 349
790 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 350
791 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 351
792 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 352 |  |  |  | AC CMR to be used
793 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 353
794 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 354
795 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10019
796 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10019
797 | Thakur Tala | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 355
798 | Thakur Tala | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 356
799 | Thakur Tala | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 357
800 | Thakur Tala | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 358
801 | Thakur Tala | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 359
802 | Thakur Tala | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 360
803 | Thakur Tala | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 361
804 | Thakur Tala | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 362
805 | Thakur Tala | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 363
806 | Thakur Tala | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 364
807 | Thakur Tala | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 365
808 | Thakur Tala | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 366
809 | Thakur Tala | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 367
810 | Thakur Tala | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 368
811 | Thakur Tala | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
812 | Thakur Tala | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
813 | Thakur Tala | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
814 | Thakur Tala | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
815 | Thakur Tala | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
816 | Thakur Tala | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5334
817 | Thakur Tala | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5335
818 | Thakur Tala | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5336
819 | Thakur Tala | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5337
820 | Thakur Tala | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5338
821 | Thakur Tala | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5339
822 | Thakur Tala | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5340
823 | Thakur Tala | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5341
824 | Thakur Tala | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5342
825 | Thakur Tala | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5343
826 | Thakur Tala | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5344
827 | Thakur Tala | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5345
828 | Thakur Tala | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5346
829 | Thakur Tala | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5347
830 | Thakur Tala | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5348
831 | Thakur Tala | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5349
832 | Thakur Tala | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5350
833 | Belghoria | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 369
834 | Belghoria | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 370
835 | Belghoria | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 371
836 | Belghoria | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 372
837 | Belghoria | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 373
838 | Belghoria | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 374
839 | Belghoria | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 375
840 | Belghoria | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 376
841 | Belghoria | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 377
842 | Belghoria | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 378
843 | Belghoria | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 379
844 | Belghoria | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 380
845 | Belghoria | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 381
846 | Belghoria | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 382
847 | Belghoria | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
848 | Belghoria | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
849 | Belghoria | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
850 | Belghoria | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
851 | Belghoria | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
852 | Belghoria | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5351
853 | Belghoria | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5352
854 | Belghoria | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5353
855 | Belghoria | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5354
856 | Belghoria | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5355
857 | Belghoria | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5356
858 | Belghoria | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5357
859 | Belghoria | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5358
860 | Belghoria | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5359
861 | Belghoria | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5360
862 | Belghoria | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5361
863 | Belghoria | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5362
864 | Belghoria | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5363
865 | Belghoria | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5364
866 | Belghoria | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5365
867 | Belghoria | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5366
868 | Belghoria | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5367
869 | Trikon Park | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 383
870 | Trikon Park | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 384
871 | Trikon Park | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 385
872 | Trikon Park | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 386
873 | Trikon Park | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 387
874 | Trikon Park | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 388
875 | Trikon Park | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 389
876 | Trikon Park | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 390
877 | Trikon Park | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 391
878 | Trikon Park | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 392
879 | Trikon Park | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 393
880 | Trikon Park | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 394
881 | Trikon Park | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 395
882 | Trikon Park | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 396
883 | Trikon Park | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
884 | Trikon Park | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
885 | Trikon Park | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
886 | Trikon Park | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
887 | Trikon Park | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
888 | Trikon Park | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5368
889 | Trikon Park | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5369
890 | Trikon Park | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5370
891 | Trikon Park | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5371
892 | Trikon Park | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5372
893 | Trikon Park | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5373
894 | Trikon Park | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5374
895 | Trikon Park | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5375
896 | Trikon Park | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5376
897 | Trikon Park | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5377
898 | Trikon Park | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5378
899 | Trikon Park | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5379
900 | Trikon Park | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5380
901 | Trikon Park | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5381
902 | Trikon Park | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5382
903 | Trikon Park | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5383
904 | Trikon Park | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5384
905 | Incomer-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 397
906 | Incomer-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 398
907 | Incomer-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 399
908 | Incomer-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 400
909 | Incomer-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 401
910 | Incomer-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 402
911 | Incomer-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 403
912 | Incomer-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 404
913 | Incomer-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 405
914 | Incomer-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 406
915 | Incomer-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 407
916 | Incomer-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 408
917 | Incomer-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 409
918 | Incomer-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
919 | Incomer-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
920 | Incomer-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
921 | Incomer-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13076
922 | Incomer-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13077
923 | Incomer-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5385
924 | Incomer-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5386
925 | Incomer-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5387
926 | Incomer-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5388
927 | Incomer-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5389
928 | Incomer-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5390
929 | Incomer-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5391
930 | Incomer-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5392
931 | Incomer-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5393
932 | Incomer-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5394
933 | Incomer-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5395
934 | Incomer-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5396
935 | Incomer-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5397
936 | Incomer-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5398
937 | Incomer-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5399
938 | Incomer-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5400
939 | Incomer-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5401
940 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 410
941 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 411
942 | Bus Coupler-3 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 412
943 | Bus Coupler-3 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 413
944 | Bus Coupler-3 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 414
945 | Bus Coupler-3 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 415
946 | Bus Coupler-3 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 416
947 | Bus Coupler-3 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 417 |  |  |  | AC CMR to be used
948 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 418
949 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 419
950 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10024
951 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10024
952 | Jana Nagari | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 420
953 | Jana Nagari | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 421
954 | Jana Nagari | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 422
955 | Jana Nagari | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 423
956 | Jana Nagari | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 424
957 | Jana Nagari | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 425
958 | Jana Nagari | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 426
959 | Jana Nagari | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 427
960 | Jana Nagari | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 428
961 | Jana Nagari | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 429
962 | Jana Nagari | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 430
963 | Jana Nagari | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 431
964 | Jana Nagari | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 432
965 | Jana Nagari | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 433
966 | Jana Nagari | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10025
967 | Jana Nagari | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10025
968 | Jana Nagari | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
969 | Jana Nagari | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13079
970 | Jana Nagari | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13080
971 | Jana Nagari | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5402
972 | Jana Nagari | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5403
973 | Jana Nagari | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5404
974 | Jana Nagari | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5405
975 | Jana Nagari | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5406
976 | Jana Nagari | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5407
977 | Jana Nagari | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5408
978 | Jana Nagari | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5409
979 | Jana Nagari | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5410
980 | Jana Nagari | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5411
981 | Jana Nagari | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5412
982 | Jana Nagari | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5413
983 | Jana Nagari | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5414
984 | Jana Nagari | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5415
985 | Jana Nagari | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5416
986 | Jana Nagari | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5417
987 | Jana Nagari | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5418
988 | GoleBagan | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 434
989 | GoleBagan | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 435
990 | GoleBagan | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 436
991 | GoleBagan | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 437
992 | GoleBagan | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 438
993 | GoleBagan | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 439
994 | GoleBagan | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 440
995 | GoleBagan | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 441
996 | GoleBagan | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 442
997 | GoleBagan | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 443
998 | GoleBagan | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 444
999 | GoleBagan | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 445
1000 | GoleBagan | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 446
1001 | GoleBagan | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 447
1002 | GoleBagan | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
1003 | GoleBagan | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
1004 | GoleBagan | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
1005 | GoleBagan | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13082
1006 | GoleBagan | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13083
1007 | GoleBagan | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5419
1008 | GoleBagan | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5420
1009 | GoleBagan | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5421
1010 | GoleBagan | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5422
1011 | GoleBagan | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5423
1012 | GoleBagan | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5424
1013 | GoleBagan | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5425
1014 | GoleBagan | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5426
1015 | GoleBagan | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5427
1016 | GoleBagan | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5428
1017 | GoleBagan | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5429
1018 | GoleBagan | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5430
1019 | GoleBagan | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5431
1020 | GoleBagan | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5432
1021 | GoleBagan | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5433
1022 | GoleBagan | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5434
1023 | GoleBagan | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5435
1024 | Spare-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 448
1025 | Spare-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 449
1026 | Spare-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 450
1027 | Spare-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 451
1028 | Spare-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 452
1029 | Spare-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 453
1030 | Spare-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 454
1031 | Spare-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 455
1032 | Spare-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 456
1033 | Spare-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 457
1034 | Spare-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 458
1035 | Spare-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 459
1036 | Spare-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 460
1037 | Spare-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 461
1038 | Spare-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10027
1039 | Spare-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10027
1040 | Spare-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1041 | Spare-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1042 | Spare-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13086
1043 | Spare-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5436
1044 | Spare-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5437
1045 | Spare-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5438
1046 | Spare-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5439
1047 | Spare-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5440
1048 | Spare-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5441
1049 | Spare-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5442
1050 | Spare-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5443
1051 | Spare-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5444
1052 | Spare-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5445
1053 | Spare-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5446
1054 | Spare-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5447
1055 | Spare-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5448
1056 | Spare-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5449
1057 | Spare-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5450
1058 | Spare-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5451
1059 | Spare-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5452
1060 | Incomer-4 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 462
1061 | Incomer-4 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 463
1062 | Incomer-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 464
1063 | Incomer-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 465
1064 | Incomer-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 466
1065 | Incomer-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 467
1066 | Incomer-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 468
1067 | Incomer-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 469
1068 | Incomer-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 470
1069 | Incomer-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 471
1070 | Incomer-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 472
1071 | Incomer-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 473
1072 | Incomer-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 474
1073 | Incomer-4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10028
1074 | Incomer-4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10028
1075 | Incomer-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1076 | Incomer-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1077 | Incomer-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13089
1078 | Incomer-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5453
1079 | Incomer-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5454
1080 | Incomer-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5455
1081 | Incomer-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5456
1082 | Incomer-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5457
1083 | Incomer-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5458
1084 | Incomer-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5459
1085 | Incomer-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5460
1086 | Incomer-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5461
1087 | Incomer-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5462
1088 | Incomer-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5463
1089 | Incomer-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5464
1090 | Incomer-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5465
1091 | Incomer-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5466
1092 | Incomer-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5467
1093 | Incomer-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5468
1094 | Incomer-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5469
1095 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 475
1096 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 476
1097 | Bus Coupler-4 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 477
1098 | Bus Coupler-4 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 478
1099 | Bus Coupler-4 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 479
1100 | Bus Coupler-4 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 480
1101 | Bus Coupler-4 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 481
1102 | Bus Coupler-4 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 482 |  |  |  | AC CMR to be used
1103 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 483
1104 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 484
1105 | Bus Coupler-4 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10029
1106 | Bus Coupler-4 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10029
1107 | Nandan Nagar | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 485
1108 | Nandan Nagar | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 486
1109 | Nandan Nagar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 487
1110 | Nandan Nagar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 488
1111 | Nandan Nagar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 489
1112 | Nandan Nagar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 490
1113 | Nandan Nagar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 491
1114 | Nandan Nagar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 492
1115 | Nandan Nagar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 493
1116 | Nandan Nagar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 494
1117 | Nandan Nagar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 495
1118 | Nandan Nagar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 496
1119 | Nandan Nagar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 497
1120 | Nandan Nagar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 498
1121 | Nandan Nagar | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10030
1122 | Nandan Nagar | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10030
1123 | Nandan Nagar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1124 | Nandan Nagar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1125 | Nandan Nagar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13092
1126 | Nandan Nagar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5470
1127 | Nandan Nagar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5471
1128 | Nandan Nagar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5472
1129 | Nandan Nagar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5473
1130 | Nandan Nagar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5474
1131 | Nandan Nagar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5475
1132 | Nandan Nagar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5476
1133 | Nandan Nagar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5477
1134 | Nandan Nagar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5478
1135 | Nandan Nagar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5479
1136 | Nandan Nagar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5480
1137 | Nandan Nagar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5481
1138 | Nandan Nagar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5482
1139 | Nandan Nagar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5483
1140 | Nandan Nagar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5484
1141 | Nandan Nagar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5485
1142 | Nandan Nagar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5486
1143 | Moha Nagar | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 499
1144 | Moha Nagar | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 500
1145 | Moha Nagar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 501
1146 | Moha Nagar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 502
1147 | Moha Nagar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 503
1148 | Moha Nagar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 504
1149 | Moha Nagar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 505
1150 | Moha Nagar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 506
1151 | Moha Nagar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 507
1152 | Moha Nagar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 508
1153 | Moha Nagar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 509
1154 | Moha Nagar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 510
1155 | Moha Nagar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 511
1156 | Moha Nagar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 512
1157 | Moha Nagar | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10031
1158 | Moha Nagar | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10031
1159 | Moha Nagar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13093
1160 | Moha Nagar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13094
1161 | Moha Nagar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13095
1162 | Moha Nagar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5487
1163 | Moha Nagar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5488
1164 | Moha Nagar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5489
1165 | Moha Nagar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5490
1166 | Moha Nagar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5491
1167 | Moha Nagar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5492
1168 | Moha Nagar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5493
1169 | Moha Nagar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5494
1170 | Moha Nagar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5495
1171 | Moha Nagar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5496
1172 | Moha Nagar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5497
1173 | Moha Nagar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5498
1174 | Moha Nagar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5499
1175 | Moha Nagar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5500
1176 | Moha Nagar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5501
1177 | Moha Nagar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5502
1178 | Moha Nagar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5503
1179 | Incomer-5 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 513
1180 | Incomer-5 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 514
1181 | Incomer-5 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 515
1182 | Incomer-5 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 516
1183 | Incomer-5 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 517
1184 | Incomer-5 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 518
1185 | Incomer-5 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 519
1186 | Incomer-5 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 520
1187 | Incomer-5 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 521
1188 | Incomer-5 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 522
1189 | Incomer-5 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 523
1190 | Incomer-5 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 524
1191 | Incomer-5 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 525
1192 | Incomer-5 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10032
1193 | Incomer-5 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10032
1194 | Incomer-5 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13096
1195 | Incomer-5 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13097
1196 | Incomer-5 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13098
1197 | Incomer-5 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5504
1198 | Incomer-5 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5505
1199 | Incomer-5 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5506
1200 | Incomer-5 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5507
1201 | Incomer-5 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5508
1202 | Incomer-5 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5509
1203 | Incomer-5 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5510
1204 | Incomer-5 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5511
1205 | Incomer-5 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5512
1206 | Incomer-5 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5513
1207 | Incomer-5 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5514
1208 | Incomer-5 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5515
1209 | Incomer-5 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5516
1210 | Incomer-5 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5517
1211 | Incomer-5 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5518
1212 | Incomer-5 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5519
1213 | Incomer-5 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5520
1214 | Future Transformer | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 526
1215 | Future Transformer | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 527
1216 | Future Transformer | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 528
1217 | Future Transformer | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 529
1218 | Future Transformer | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 530
1219 | Future Transformer | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 531
1220 | Future Transformer | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 532
1221 | Future Transformer | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 533
1222 | Future Transformer | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 534
1223 | Future Transformer | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 535
1224 | Future Transformer | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 536
1225 | Future Transformer | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 537
1226 | Future Transformer | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 538
1227 | Future Transformer | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 539
1228 | Future Transformer | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 540
1229 | Future Transformer | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 541
1230 | Future Transformer | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 542
1231 | Future Transformer | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 543
1232 | Future Transformer | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 544
1233 | Future Transformer | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 545
1234 | Future Transformer | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 546
1235 | Future Transformer | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 547
1236 | Future Transformer | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 548
1237 | Future Transformer | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 549
1238 | Future Transformer | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13099
1239 | Future Transformer | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13100
1240 | Future Transformer | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13101
1241 | Future Transformer | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13102
1242 | Future Transformer | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10033
1243 | Future Transformer | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10033
1244 | Future Transformer | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5521
1245 | Future Transformer | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5522
1246 | Future Transformer | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5523
1247 | Future Transformer | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5524
1248 | Future Transformer | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5525
1249 | Future Transformer | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5526
1250 | Future Transformer | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5527
1251 | Future Transformer | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5528
1252 | Future Transformer | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5529
1253 | Future Transformer | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5530
1254 | Future Transformer | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5531
1255 | Future Transformer | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5532
1256 | Future Transformer | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5533
1257 | Future Transformer | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5534
1258 | Future Transformer | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5535
1259 | Future Transformer | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5536
1260 | Future Transformer | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5537
1261 | Future Transformer(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 550
1262 | Future Transformer(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 551
1263 | Future Transformer(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 552 |  |  |  | AC CMR to be used
1264 | Future Transformer(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 553
1265 | Future Transformer(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 554
1266 | Future Transformer(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 555
1267 | Future Transformer(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 556
1268 | Future Transformer(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 557
1269 | Future Transformer(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13103
1270 | Future Transformer(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13104
1271 | Future Transformer(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5538
1272 | Future Transformer(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5539
1273 | Future Transformer(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5540
1274 | Future 11kV O/G-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 558
1275 | Future 11kV O/G-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 559
1276 | Future 11kV O/G-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 560
1277 | Future 11kV O/G-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 561
1278 | Future 11kV O/G-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 562
1279 | Future 11kV O/G-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 563
1280 | Future 11kV O/G-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 564
1281 | Future 11kV O/G-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 565
1282 | Future 11kV O/G-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 566
1283 | Future 11kV O/G-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 567
1284 | Future 11kV O/G-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 568
1285 | Future 11kV O/G-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 569
1286 | Future 11kV O/G-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 570
1287 | Future 11kV O/G-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 571
1288 | Future 11kV O/G-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10034
1289 | Future 11kV O/G-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10034
1290 | Future 11kV O/G-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13105
1291 | Future 11kV O/G-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13106
1292 | Future 11kV O/G-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13107
1293 | Future 11kV O/G-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5541
1294 | Future 11kV O/G-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5542
1295 | Future 11kV O/G-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5543
1296 | Future 11kV O/G-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5544
1297 | Future 11kV O/G-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5545
1298 | Future 11kV O/G-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5546
1299 | Future 11kV O/G-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5547
1300 | Future 11kV O/G-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5548
1301 | Future 11kV O/G-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5549
1302 | Future 11kV O/G-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5550
1303 | Future 11kV O/G-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5551
1304 | Future 11kV O/G-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5552
1305 | Future 11kV O/G-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5553
1306 | Future 11kV O/G-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5554
1307 | Future 11kV O/G-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5555
1308 | Future 11kV O/G-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5556
1309 | Future 11kV O/G-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5557
1310 | Future 11kV O/G-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 572
1311 | Future 11kV O/G-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 573
1312 | Future 11kV O/G-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 574
1313 | Future 11kV O/G-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 575
1314 | Future 11kV O/G-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 576
1315 | Future 11kV O/G-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 577
1316 | Future 11kV O/G-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 578
1317 | Future 11kV O/G-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 579
1318 | Future 11kV O/G-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 580
1319 | Future 11kV O/G-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 581
1320 | Future 11kV O/G-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 582
1321 | Future 11kV O/G-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 583
1322 | Future 11kV O/G-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 584
1323 | Future 11kV O/G-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 585
1324 | Future 11kV O/G-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10035
1325 | Future 11kV O/G-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10035
1326 | Future 11kV O/G-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13108
1327 | Future 11kV O/G-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13109
1328 | Future 11kV O/G-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13110
1329 | Future 11kV O/G-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5558
1330 | Future 11kV O/G-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5559
1331 | Future 11kV O/G-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5560
1332 | Future 11kV O/G-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5561
1333 | Future 11kV O/G-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5562
1334 | Future 11kV O/G-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5563
1335 | Future 11kV O/G-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5564
1336 | Future 11kV O/G-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5565
1337 | Future 11kV O/G-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5566
1338 | Future 11kV O/G-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5567
1339 | Future 11kV O/G-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5568
1340 | Future 11kV O/G-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5569
1341 | Future 11kV O/G-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5570
1342 | Future 11kV O/G-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5571
1343 | Future 11kV O/G-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5572
1344 | Future 11kV O/G-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5573
1345 | Future 11kV O/G-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5574
1346 | Future 11kV O/G-3 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 586
1347 | Future 11kV O/G-3 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 587
1348 | Future 11kV O/G-3 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 588
1349 | Future 11kV O/G-3 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 589
1350 | Future 11kV O/G-3 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 590
1351 | Future 11kV O/G-3 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 591
1352 | Future 11kV O/G-3 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 592
1353 | Future 11kV O/G-3 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 593
1354 | Future 11kV O/G-3 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 594
1355 | Future 11kV O/G-3 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 595
1356 | Future 11kV O/G-3 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 596
1357 | Future 11kV O/G-3 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 597
1358 | Future 11kV O/G-3 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 598
1359 | Future 11kV O/G-3 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 599
1360 | Future 11kV O/G-3 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10036
1361 | Future 11kV O/G-3 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10036
1362 | Future 11kV O/G-3 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13111
1363 | Future 11kV O/G-3 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13112
1364 | Future 11kV O/G-3 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13113
1365 | Future 11kV O/G-3 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5575
1366 | Future 11kV O/G-3 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5576
1367 | Future 11kV O/G-3 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5577
1368 | Future 11kV O/G-3 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5578
1369 | Future 11kV O/G-3 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5579
1370 | Future 11kV O/G-3 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5580
1371 | Future 11kV O/G-3 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5581
1372 | Future 11kV O/G-3 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5582
1373 | Future 11kV O/G-3 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5583
1374 | Future 11kV O/G-3 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5584
1375 | Future 11kV O/G-3 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5585
1376 | Future 11kV O/G-3 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5586
1377 | Future 11kV O/G-3 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5587
1378 | Future 11kV O/G-3 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5588
1379 | Future 11kV O/G-3 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5589
1380 | Future 11kV O/G-3 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5590
1381 | Future 11kV O/G-3 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5591
1382 | Future 11kV O/G-4 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 600
1383 | Future 11kV O/G-4 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 601
1384 | Future 11kV O/G-4 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 602
1385 | Future 11kV O/G-4 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 603
1386 | Future 11kV O/G-4 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 604
1387 | Future 11kV O/G-4 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 605
1388 | Future 11kV O/G-4 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 606
1389 | Future 11kV O/G-4 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 607
1390 | Future 11kV O/G-4 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 608
1391 | Future 11kV O/G-4 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 609
1392 | Future 11kV O/G-4 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 610
1393 | Future 11kV O/G-4 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 611
1394 | Future 11kV O/G-4 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 612
1395 | Future 11kV O/G-4 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 613
1396 | Future 11kV O/G-4 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10037
1397 | Future 11kV O/G-4 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10037
1398 | Future 11kV O/G-4 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13114
1399 | Future 11kV O/G-4 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13115
1400 | Future 11kV O/G-4 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13116
1401 | Future 11kV O/G-4 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5592
1402 | Future 11kV O/G-4 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5593
1403 | Future 11kV O/G-4 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5594
1404 | Future 11kV O/G-4 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5595
1405 | Future 11kV O/G-4 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5596
1406 | Future 11kV O/G-4 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5597
1407 | Future 11kV O/G-4 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5598
1408 | Future 11kV O/G-4 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5599
1409 | Future 11kV O/G-4 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5600
1410 | Future 11kV O/G-4 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5601
1411 | Future 11kV O/G-4 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5602
1412 | Future 11kV O/G-4 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5603
1413 | Future 11kV O/G-4 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5604
1414 | Future 11kV O/G-4 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5605
1415 | Future 11kV O/G-4 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5606
1416 | Future 11kV O/G-4 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5607
1417 | Future 11kV O/G-4 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5608
1418 | Future 11kV Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 614
1419 | Future 11kV Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 615
1420 | Future 11kV Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 616
1421 | Future 11kV Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 617
1422 | Future 11kV Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 618
1423 | Future 11kV Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 619
1424 | Future 11kV Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 620
1425 | Future 11kV Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 621
1426 | Future 11kV Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 622
1427 | Future 11kV Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 623
1428 | Future 11kV Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 624
1429 | Future 11kV Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 625
1430 | Future 11kV Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 626
1431 | Future 11kV Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10038
1432 | Future 11kV Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10038
1433 | Future 11kV Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13117
1434 | Future 11kV Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13118
1435 | Future 11kV Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13119
1436 | Future 11kV Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5609
1437 | Future 11kV Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5610
1438 | Future 11kV Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5611
1439 | Future 11kV Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5612
1440 | Future 11kV Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5613
1441 | Future 11kV Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5614
1442 | Future 11kV Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5615
1443 | Future 11kV Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5616
1444 | Future 11kV Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5617
1445 | Future 11kV Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5618
1446 | Future 11kV Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5619
1447 | Future 11kV Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5620
1448 | Future 11kV Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5621
1449 | Future 11kV Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5622
1450 | Future 11kV Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5623
1451 | Future 11kV Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5624
1452 | Future 11kV Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5625
1453 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 627
1454 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 628
1455 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 629
1456 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 630
1457 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 631
1458 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 632
1459 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 633
1460 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 634 |  |  |  | AC CMR to be used
1461 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 635
1462 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 636
1463 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10039
1464 | Future 11kV Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10039