## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub_Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Sub_Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Sub_Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub_Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub_Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub_Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | Mohispota CKT-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 112
209 | Mohispota CKT-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 113
210 | Mohispota CKT-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 114
211 | Mohispota CKT-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 115
212 | Mohispota CKT-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 116
213 | Mohispota CKT-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 117
214 | Mohispota CKT-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 118
215 | Mohispota CKT-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 119
216 | Mohispota CKT-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 120
217 | Mohispota CKT-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 121
218 | Mohispota CKT-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 122
219 | Mohispota CKT-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 123
220 | Mohispota CKT-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
221 | Mohispota CKT-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13019
222 | Mohispota CKT-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13020
223 | Mohispota CKT-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10004
224 | Mohispota CKT-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10004
225 | Mohispota CKT-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5068
226 | Mohispota CKT-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5069
227 | Mohispota CKT-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5070
228 | Mohispota CKT-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5071
229 | Mohispota CKT-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5072
230 | Mohispota CKT-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5073
231 | Mohispota CKT-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5074
232 | Mohispota CKT-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5075
233 | Mohispota CKT-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5076
234 | Mohispota CKT-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5077
235 | Mohispota CKT-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5078
236 | Mohispota CKT-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5079
237 | Mohispota CKT-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5080
238 | Mohispota CKT-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5081
239 | Mohispota CKT-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5082
240 | Mohispota CKT-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
241 | Mohispota CKT-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
242 | Mohispota CKT-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5085
243 | Mohispota CKT-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5086
244 | Agharpara CKT-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 124
245 | Agharpara CKT-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 125
246 | Agharpara CKT-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 126
247 | Agharpara CKT-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 127
248 | Agharpara CKT-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 128
249 | Agharpara CKT-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 129
250 | Agharpara CKT-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 130
251 | Agharpara CKT-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 131
252 | Agharpara CKT-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 132
253 | Agharpara CKT-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 133
254 | Agharpara CKT-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 134
255 | Agharpara CKT-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 135
256 | Agharpara CKT-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
257 | Agharpara CKT-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13022
258 | Agharpara CKT-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13023
259 | Agharpara CKT-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
260 | Agharpara CKT-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
261 | Agharpara CKT-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5087
262 | Agharpara CKT-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5088
263 | Agharpara CKT-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5089
264 | Agharpara CKT-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5090
265 | Agharpara CKT-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5091
266 | Agharpara CKT-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5092
267 | Agharpara CKT-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5093
268 | Agharpara CKT-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5094
269 | Agharpara CKT-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5095
270 | Agharpara CKT-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5096
271 | Agharpara CKT-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5097
272 | Agharpara CKT-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5098
273 | Agharpara CKT-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5099
274 | Agharpara CKT-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5100
275 | Agharpara CKT-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5101
276 | Agharpara CKT-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5102
277 | Agharpara CKT-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5103
278 | Agharpara CKT-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5104
279 | Agharpara CKT-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5105
280 | Mohispota CKT-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 136
281 | Mohispota CKT-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 137
282 | Mohispota CKT-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 138
283 | Mohispota CKT-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 139
284 | Mohispota CKT-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 140
285 | Mohispota CKT-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 141
286 | Mohispota CKT-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 142
287 | Mohispota CKT-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 143
288 | Mohispota CKT-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 144
289 | Mohispota CKT-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 145
290 | Mohispota CKT-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 146
291 | Mohispota CKT-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 147
292 | Mohispota CKT-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
293 | Mohispota CKT-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
294 | Mohispota CKT-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
295 | Mohispota CKT-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
296 | Mohispota CKT-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
297 | Mohispota CKT-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5106
298 | Mohispota CKT-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5107
299 | Mohispota CKT-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5108
300 | Mohispota CKT-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5109
301 | Mohispota CKT-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5110
302 | Mohispota CKT-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5111
303 | Mohispota CKT-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5112
304 | Mohispota CKT-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5113
305 | Mohispota CKT-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5114
306 | Mohispota CKT-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5115
307 | Mohispota CKT-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5116
308 | Mohispota CKT-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5117
309 | Mohispota CKT-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5118
310 | Mohispota CKT-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5119
311 | Mohispota CKT-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5120
312 | Mohispota CKT-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5121
313 | Mohispota CKT-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5122
314 | Mohispota CKT-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5123
315 | Mohispota CKT-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5124
316 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 148
317 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 149
318 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 150
319 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 151
320 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 152
321 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 153
322 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 154
323 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 155
324 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 156
325 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 157
326 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 158
327 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 159
328 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 160
329 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
330 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
331 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
332 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
333 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13029
334 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5125
335 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5126
336 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5127
337 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5128
338 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5129
339 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5130
340 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5131
341 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5132
342 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5133
343 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5134
344 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5135
345 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5136
346 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5137
347 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5138
348 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5139
349 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5140
350 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5141
351 | Sukanta pally | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 161
352 | Sukanta pally | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 162
353 | Sukanta pally | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 163
354 | Sukanta pally | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 164
355 | Sukanta pally | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 165
356 | Sukanta pally | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 166
357 | Sukanta pally | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 167
358 | Sukanta pally | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 168
359 | Sukanta pally | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 169
360 | Sukanta pally | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 170
361 | Sukanta pally | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 171
362 | Sukanta pally | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 172
363 | Sukanta pally | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 173
364 | Sukanta pally | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 174
365 | Sukanta pally | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
366 | Sukanta pally | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
367 | Sukanta pally | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
368 | Sukanta pally | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
369 | Sukanta pally | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13032
370 | Sukanta pally | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5142
371 | Sukanta pally | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5143
372 | Sukanta pally | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5144
373 | Sukanta pally | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5145
374 | Sukanta pally | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5146
375 | Sukanta pally | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5147
376 | Sukanta pally | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5148
377 | Sukanta pally | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5149
378 | Sukanta pally | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5150
379 | Sukanta pally | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5151
380 | Sukanta pally | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5152
381 | Sukanta pally | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5153
382 | Sukanta pally | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5154
383 | Sukanta pally | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5155
384 | Sukanta pally | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5156
385 | Sukanta pally | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5157
386 | Sukanta pally | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5158
387 | Cotton mill | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 175
388 | Cotton mill | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 176
389 | Cotton mill | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 177
390 | Cotton mill | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 178
391 | Cotton mill | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 179
392 | Cotton mill | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 180
393 | Cotton mill | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 181
394 | Cotton mill | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 182
395 | Cotton mill | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 183
396 | Cotton mill | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 184
397 | Cotton mill | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 185
398 | Cotton mill | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 186
399 | Cotton mill | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 187
400 | Cotton mill | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 188
401 | Cotton mill | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
402 | Cotton mill | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
403 | Cotton mill | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
404 | Cotton mill | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
405 | Cotton mill | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13035
406 | Cotton mill | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5159
407 | Cotton mill | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5160
408 | Cotton mill | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5161
409 | Cotton mill | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5162
410 | Cotton mill | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5163
411 | Cotton mill | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5164
412 | Cotton mill | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5165
413 | Cotton mill | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5166
414 | Cotton mill | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5167
415 | Cotton mill | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5168
416 | Cotton mill | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5169
417 | Cotton mill | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5170
418 | Cotton mill | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5171
419 | Cotton mill | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5172
420 | Cotton mill | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5173
421 | Cotton mill | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5174
422 | Cotton mill | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5175
423 | Kadam tala | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 189
424 | Kadam tala | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 190
425 | Kadam tala | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 191
426 | Kadam tala | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 192
427 | Kadam tala | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 193
428 | Kadam tala | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 194
429 | Kadam tala | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 195
430 | Kadam tala | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 196
431 | Kadam tala | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 197
432 | Kadam tala | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 198
433 | Kadam tala | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 199
434 | Kadam tala | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 200
435 | Kadam tala | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 201
436 | Kadam tala | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 202
437 | Kadam tala | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
438 | Kadam tala | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
439 | Kadam tala | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
440 | Kadam tala | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
441 | Kadam tala | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
442 | Kadam tala | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5176
443 | Kadam tala | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5177
444 | Kadam tala | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5178
445 | Kadam tala | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5179
446 | Kadam tala | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5180
447 | Kadam tala | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5181
448 | Kadam tala | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5182
449 | Kadam tala | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5183
450 | Kadam tala | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5184
451 | Kadam tala | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5185
452 | Kadam tala | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5186
453 | Kadam tala | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5187
454 | Kadam tala | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5188
455 | Kadam tala | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5189
456 | Kadam tala | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5190
457 | Kadam tala | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5191
458 | Kadam tala | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5192
459 | Hospital | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 203
460 | Hospital | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 204
461 | Hospital | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 205
462 | Hospital | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 206
463 | Hospital | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 207
464 | Hospital | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 208
465 | Hospital | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 209
466 | Hospital | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 210
467 | Hospital | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 211
468 | Hospital | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 212
469 | Hospital | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 213
470 | Hospital | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 214
471 | Hospital | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 215
472 | Hospital | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 216
473 | Hospital | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
474 | Hospital | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
475 | Hospital | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
476 | Hospital | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
477 | Hospital | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
478 | Hospital | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5193
479 | Hospital | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5194
480 | Hospital | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5195
481 | Hospital | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5196
482 | Hospital | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5197
483 | Hospital | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5198
484 | Hospital | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5199
485 | Hospital | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5200
486 | Hospital | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5201
487 | Hospital | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5202
488 | Hospital | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5203
489 | Hospital | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5204
490 | Hospital | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5205
491 | Hospital | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5206
492 | Hospital | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5207
493 | Hospital | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5208
494 | Hospital | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5209
495 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 217
496 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 218
497 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 219
498 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 220
499 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 221
500 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 222
501 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 223
502 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 224 |  |  |  | AC CMR to be used
503 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 225
504 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 226
505 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10012
506 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10012
507 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 227
508 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 228
509 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 229
510 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 230
511 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 231
512 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 232
513 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 233
514 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 234
515 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 235
516 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 236
517 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 237
518 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 238
519 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 239
520 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
521 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
522 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
523 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13043
524 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13044
525 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5210
526 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5211
527 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5212
528 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5213
529 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5214
530 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5215
531 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5216
532 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5217
533 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5218
534 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5219
535 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5220
536 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5221
537 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5222
538 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5223
539 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5224
540 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5225
541 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5226
542 | Muragacha | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 240
543 | Muragacha | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 241
544 | Muragacha | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 242
545 | Muragacha | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 243
546 | Muragacha | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 244
547 | Muragacha | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 245
548 | Muragacha | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 246
549 | Muragacha | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 247
550 | Muragacha | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 248
551 | Muragacha | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 249
552 | Muragacha | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 250
553 | Muragacha | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 251
554 | Muragacha | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 252
555 | Muragacha | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 253
556 | Muragacha | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
557 | Muragacha | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
558 | Muragacha | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
559 | Muragacha | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
560 | Muragacha | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
561 | Muragacha | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5227
562 | Muragacha | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5228
563 | Muragacha | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5229
564 | Muragacha | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5230
565 | Muragacha | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5231
566 | Muragacha | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5232
567 | Muragacha | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5233
568 | Muragacha | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5234
569 | Muragacha | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5235
570 | Muragacha | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5236
571 | Muragacha | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5237
572 | Muragacha | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5238
573 | Muragacha | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5239
574 | Muragacha | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5240
575 | Muragacha | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5241
576 | Muragacha | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5242
577 | Muragacha | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5243
578 | Ramchandra pur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 254
579 | Ramchandra pur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 255
580 | Ramchandra pur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 256
581 | Ramchandra pur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 257
582 | Ramchandra pur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 258
583 | Ramchandra pur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 259
584 | Ramchandra pur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 260
585 | Ramchandra pur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 261
586 | Ramchandra pur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 262
587 | Ramchandra pur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 263
588 | Ramchandra pur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 264
589 | Ramchandra pur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 265
590 | Ramchandra pur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 266
591 | Ramchandra pur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 267
592 | Ramchandra pur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
593 | Ramchandra pur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
594 | Ramchandra pur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
595 | Ramchandra pur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
596 | Ramchandra pur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
597 | Ramchandra pur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5244
598 | Ramchandra pur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5245
599 | Ramchandra pur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5246
600 | Ramchandra pur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5247
601 | Ramchandra pur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5248
602 | Ramchandra pur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5249
603 | Ramchandra pur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5250
604 | Ramchandra pur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5251
605 | Ramchandra pur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5252
606 | Ramchandra pur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5253
607 | Ramchandra pur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5254
608 | Ramchandra pur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5255
609 | Ramchandra pur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5256
610 | Ramchandra pur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5257
611 | Ramchandra pur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5258
612 | Ramchandra pur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5259
613 | Ramchandra pur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5260
614 | H.B Town | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 268
615 | H.B Town | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 269
616 | H.B Town | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 270
617 | H.B Town | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 271
618 | H.B Town | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 272
619 | H.B Town | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 273
620 | H.B Town | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 274
621 | H.B Town | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 275
622 | H.B Town | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 276
623 | H.B Town | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 277
624 | H.B Town | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 278
625 | H.B Town | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 279
626 | H.B Town | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 280
627 | H.B Town | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 281
628 | H.B Town | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
629 | H.B Town | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
630 | H.B Town | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
631 | H.B Town | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
632 | H.B Town | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
633 | H.B Town | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5261
634 | H.B Town | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5262
635 | H.B Town | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5263
636 | H.B Town | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5264
637 | H.B Town | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5265
638 | H.B Town | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5266
639 | H.B Town | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5267
640 | H.B Town | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5268
641 | H.B Town | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5269
642 | H.B Town | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5270
643 | H.B Town | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5271
644 | H.B Town | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5272
645 | H.B Town | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5273
646 | H.B Town | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5274
647 | H.B Town | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5275
648 | H.B Town | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5276
649 | H.B Town | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5277
650 | Panchanatala | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 282
651 | Panchanatala | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 283
652 | Panchanatala | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 284
653 | Panchanatala | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 285
654 | Panchanatala | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 286
655 | Panchanatala | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 287
656 | Panchanatala | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 288
657 | Panchanatala | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 289
658 | Panchanatala | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 290
659 | Panchanatala | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 291
660 | Panchanatala | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 292
661 | Panchanatala | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 293
662 | Panchanatala | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 294
663 | Panchanatala | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 295
664 | Panchanatala | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
665 | Panchanatala | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
666 | Panchanatala | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
667 | Panchanatala | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
668 | Panchanatala | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
669 | Panchanatala | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5278
670 | Panchanatala | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5279
671 | Panchanatala | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5280
672 | Panchanatala | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5281
673 | Panchanatala | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5282
674 | Panchanatala | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5283
675 | Panchanatala | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5284
676 | Panchanatala | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5285
677 | Panchanatala | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5286
678 | Panchanatala | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5287
679 | Panchanatala | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5288
680 | Panchanatala | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5289
681 | Panchanatala | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5290
682 | Panchanatala | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5291
683 | Panchanatala | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5292
684 | Panchanatala | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5293
685 | Panchanatala | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5294
686 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 296
687 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 297
688 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 298
689 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 299
690 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 300
691 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 301
692 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 302
693 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 303 |  |  |  | AC CMR to be used
694 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 304
695 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 305
696 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10018
697 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10018
698 | Incomer-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 306
699 | Incomer-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 307
700 | Incomer-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 308
701 | Incomer-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 309
702 | Incomer-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 310
703 | Incomer-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 311
704 | Incomer-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 312
705 | Incomer-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 313
706 | Incomer-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 314
707 | Incomer-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 315
708 | Incomer-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 316
709 | Incomer-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 317
710 | Incomer-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 318
711 | Incomer-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
712 | Incomer-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
713 | Incomer-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
714 | Incomer-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13058
715 | Incomer-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13059
716 | Incomer-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5295
717 | Incomer-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5296
718 | Incomer-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5297
719 | Incomer-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5298
720 | Incomer-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5299
721 | Incomer-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5300
722 | Incomer-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5301
723 | Incomer-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5302
724 | Incomer-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5303
725 | Incomer-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5304
726 | Incomer-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5305
727 | Incomer-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5306
728 | Incomer-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5307
729 | Incomer-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5308
730 | Incomer-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5309
731 | Incomer-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5310
732 | Incomer-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5311
733 | Ghola | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 319
734 | Ghola | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 320
735 | Ghola | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 321
736 | Ghola | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 322
737 | Ghola | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 323
738 | Ghola | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 324
739 | Ghola | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 325
740 | Ghola | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 326
741 | Ghola | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 327
742 | Ghola | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 328
743 | Ghola | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 329
744 | Ghola | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 330
745 | Ghola | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 331
746 | Ghola | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 332
747 | Ghola | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
748 | Ghola | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
749 | Ghola | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
750 | Ghola | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
751 | Ghola | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
752 | Ghola | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5312
753 | Ghola | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5313
754 | Ghola | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5314
755 | Ghola | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5315
756 | Ghola | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5316
757 | Ghola | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5317
758 | Ghola | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5318
759 | Ghola | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5319
760 | Ghola | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5320
761 | Ghola | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5321
762 | Ghola | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5322
763 | Ghola | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5323
764 | Ghola | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5324
765 | Ghola | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5325
766 | Ghola | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5326
767 | Ghola | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5327
768 | Ghola | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5328
769 | Ghola School | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 333
770 | Ghola School | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 334
771 | Ghola School | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 335
772 | Ghola School | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 336
773 | Ghola School | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 337
774 | Ghola School | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 338
775 | Ghola School | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 339
776 | Ghola School | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 340
777 | Ghola School | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 341
778 | Ghola School | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 342
779 | Ghola School | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 343
780 | Ghola School | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 344
781 | Ghola School | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 345
782 | Ghola School | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 346
783 | Ghola School | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
784 | Ghola School | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
785 | Ghola School | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
786 | Ghola School | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
787 | Ghola School | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
788 | Ghola School | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5329
789 | Ghola School | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5330
790 | Ghola School | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5331
791 | Ghola School | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5332
792 | Ghola School | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5333
793 | Ghola School | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5334
794 | Ghola School | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5335
795 | Ghola School | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5336
796 | Ghola School | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5337
797 | Ghola School | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5338
798 | Ghola School | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5339
799 | Ghola School | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5340
800 | Ghola School | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5341
801 | Ghola School | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5342
802 | Ghola School | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5343
803 | Ghola School | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5344
804 | Ghola School | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5345
805 | Spare-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 347
806 | Spare-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 348
807 | Spare-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 349
808 | Spare-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 350
809 | Spare-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 351
810 | Spare-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 352
811 | Spare-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 353
812 | Spare-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 354
813 | Spare-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 355
814 | Spare-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 356
815 | Spare-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 357
816 | Spare-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 358
817 | Spare-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 359
818 | Spare-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 360
819 | Spare-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
820 | Spare-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
821 | Spare-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
822 | Spare-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
823 | Spare-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
824 | Spare-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5346
825 | Spare-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5347
826 | Spare-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5348
827 | Spare-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5349
828 | Spare-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5350
829 | Spare-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5351
830 | Spare-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5352
831 | Spare-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5353
832 | Spare-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5354
833 | Spare-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5355
834 | Spare-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5356
835 | Spare-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5357
836 | Spare-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5358
837 | Spare-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5359
838 | Spare-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5360
839 | Spare-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5361
840 | Spare-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5362
841 | Panihati college | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 361
842 | Panihati college | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 362
843 | Panihati college | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 363
844 | Panihati college | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 364
845 | Panihati college | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 365
846 | Panihati college | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 366
847 | Panihati college | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 367
848 | Panihati college | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 368
849 | Panihati college | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 369
850 | Panihati college | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 370
851 | Panihati college | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 371
852 | Panihati college | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 372
853 | Panihati college | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 373
854 | Panihati college | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 374
855 | Panihati college | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
856 | Panihati college | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
857 | Panihati college | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
858 | Panihati college | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
859 | Panihati college | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
860 | Panihati college | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5363
861 | Panihati college | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5364
862 | Panihati college | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5365
863 | Panihati college | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5366
864 | Panihati college | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5367
865 | Panihati college | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5368
866 | Panihati college | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5369
867 | Panihati college | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5370
868 | Panihati college | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5371
869 | Panihati college | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5372
870 | Panihati college | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5373
871 | Panihati college | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5374
872 | Panihati college | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5375
873 | Panihati college | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5376
874 | Panihati college | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5377
875 | Panihati college | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5378
876 | Panihati college | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5379
877 | Spare | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 375
878 | Spare | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 376
879 | Spare | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 377
880 | Spare | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 378
881 | Spare | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 379
882 | Spare | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 380
883 | Spare | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 381
884 | Spare | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 382
885 | Spare | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 383
886 | Spare | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 384
887 | Spare | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 385
888 | Spare | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 386
889 | Spare | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 387
890 | Spare | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 388
891 | Spare | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
892 | Spare | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
893 | Spare | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
894 | Spare | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
895 | Spare | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
896 | Spare | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5380
897 | Spare | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5381
898 | Spare | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5382
899 | Spare | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5383
900 | Spare | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5384
901 | Spare | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5385
902 | Spare | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5386
903 | Spare | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5387
904 | Spare | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5388
905 | Spare | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5389
906 | Spare | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5390
907 | Spare | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5391
908 | Spare | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5392
909 | Spare | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5393
910 | Spare | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5394
911 | Spare | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5395
912 | Spare | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5396
913 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5397
914 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5398
915 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5399
916 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5400
917 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5401
918 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5402
919 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5403