## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | 30V DC-3 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
23 | 30V DC-3 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 15
24 | 30V DC-3 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 16
25 | 30V DC-3 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 17
26 | 30V DC-3 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 18
27 | 30V DC-3 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5008
28 | 30V DC-3 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5009
29 | 30V DC-3 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5010
30 | Substation Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
31 | Substation Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
32 | Substation Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
33 | Substation Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 19 |  |  |  | AC CMR to be used
34 | Substation Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 20
35 | Substation Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
36 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 21
37 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 22
38 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 23
39 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 24
40 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 25
41 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 26
42 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 27
43 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 28
44 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 29
45 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 30
46 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 31
47 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 32
48 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 33
49 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 34
50 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 35
51 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 36
52 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 37
53 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 38
54 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 39
55 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 40
56 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 41
57 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 42
58 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 43
59 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 44
60 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
61 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
62 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
63 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
64 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
65 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
66 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5011
67 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5012
68 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5013
69 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5014
70 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5015
71 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5016
72 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5017
73 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5018
74 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5019
75 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5020
76 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5021
77 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5022
78 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5023
79 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5024
80 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5025
81 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5026
82 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5027
83 | Transformer-1(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 45
84 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 46
85 | Transformer-1(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 47 |  |  |  | AC CMR to be used
86 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 48
87 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 49
88 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 50
89 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 51
90 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 52
91 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
92 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
93 | Transformer-1(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5028
94 | Transformer-1(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5029
95 | Transformer-1(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5030
96 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 53
97 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 54
98 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 55
99 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 56
100 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 57
101 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 58
102 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 59
103 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 60
104 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 61
105 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 62
106 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 63
107 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 64
108 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 65
109 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 66
110 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 67
111 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 68
112 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 69
113 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 70
114 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 71
115 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 72
116 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 73
117 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 74
118 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 75
119 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 76
120 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
121 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
122 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
123 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
124 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
125 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
126 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5031
127 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5032
128 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5033
129 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5034
130 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5035
131 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5036
132 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5037
133 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5038
134 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5039
135 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5040
136 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5041
137 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5042
138 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5043
139 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5044
140 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5045
141 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5046
142 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5047
143 | Transformer-2(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 77
144 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 78
145 | Transformer-2(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 79 |  |  |  | AC CMR to be used
146 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 80
147 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 81
148 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 82
149 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 83
150 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 84
151 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
152 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
153 | Transformer-2(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5048
154 | Transformer-2(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5049
155 | Transformer-2(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5050
156 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 85
157 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 86
158 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 87
159 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 88
160 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 89
161 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 90
162 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 91
163 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 92
164 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 93
165 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 94
166 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 95
167 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 96
168 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 97
169 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 98
170 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 99
171 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 100
172 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 101
173 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 102
174 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 103
175 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 104
176 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 105
177 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 106
178 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 107
179 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 108
180 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
181 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
182 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
183 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
184 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
185 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
186 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5051
187 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5052
188 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5053
189 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5054
190 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5055
191 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5056
192 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5057
193 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5058
194 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5059
195 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5060
196 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5061
197 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5062
198 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5063
199 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5064
200 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5065
201 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5066
202 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5067
203 | Transformer-3(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 109
204 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 110
205 | Transformer-3(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 111 |  |  |  | AC CMR to be used
206 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 112
207 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 113
208 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 114
209 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 115
210 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 116
211 | Transformer-3(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
212 | Transformer-3(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
213 | Transformer-3(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5068
214 | Transformer-3(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5069
215 | Transformer-3(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5070
216 | Transformer-4 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 117
217 | Transformer-4 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 118
218 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 119
219 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 120
220 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 121
221 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 122
222 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 123
223 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 124
224 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 125
225 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 126
226 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 127
227 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 128
228 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 129
229 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 130
230 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 131
231 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 132
232 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 133
233 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 134
234 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 135
235 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 136
236 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 137
237 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 138
238 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 139
239 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 140
240 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
241 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
242 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
243 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
244 | Transformer-4 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
245 | Transformer-4 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
246 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5071
247 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5072
248 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5073
249 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5074
250 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5075
251 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5076
252 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5077
253 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5078
254 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5079
255 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5080
256 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5081
257 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5082
258 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5083
259 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5084
260 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5085
261 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5086
262 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5087
263 | Transformer-4(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 141
264 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 142
265 | Transformer-4(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 143 |  |  |  | AC CMR to be used
266 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 144
267 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 145
268 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 146
269 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 147
270 | Transformer-4(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 148
271 | Transformer-4(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
272 | Transformer-4(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
273 | Transformer-4(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5088
274 | Transformer-4(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5089
275 | Transformer-4(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5090
276 | Transformer-5 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 149
277 | Transformer-5 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 150
278 | Transformer-5 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 151
279 | Transformer-5 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 152
280 | Transformer-5 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 153
281 | Transformer-5 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 154
282 | Transformer-5 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 155
283 | Transformer-5 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 156
284 | Transformer-5 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 157
285 | Transformer-5 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 158
286 | Transformer-5 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 159
287 | Transformer-5 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 160
288 | Transformer-5 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 161
289 | Transformer-5 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 162
290 | Transformer-5 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 163
291 | Transformer-5 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 164
292 | Transformer-5 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 165
293 | Transformer-5 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 166
294 | Transformer-5 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 167
295 | Transformer-5 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 168
296 | Transformer-5 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 169
297 | Transformer-5 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 170
298 | Transformer-5 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 171
299 | Transformer-5 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 172
300 | Transformer-5 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13024
301 | Transformer-5 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13025
302 | Transformer-5 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13026
303 | Transformer-5 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13027
304 | Transformer-5 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10005
305 | Transformer-5 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10005
306 | Transformer-5 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5091
307 | Transformer-5 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5092
308 | Transformer-5 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5093
309 | Transformer-5 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5094
310 | Transformer-5 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5095
311 | Transformer-5 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5096
312 | Transformer-5 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5097
313 | Transformer-5 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5098
314 | Transformer-5 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5099
315 | Transformer-5 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5100
316 | Transformer-5 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5101
317 | Transformer-5 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5102
318 | Transformer-5 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5103
319 | Transformer-5 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5104
320 | Transformer-5 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5105
321 | Transformer-5 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5106
322 | Transformer-5 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5107
323 | Transformer-5(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 173
324 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 174
325 | Transformer-5(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 175 |  |  |  | AC CMR to be used
326 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 176
327 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 177
328 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 178
329 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 179
330 | Transformer-5(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 180
331 | Transformer-5(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13028
332 | Transformer-5(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13029
333 | Transformer-5(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5108
334 | Transformer-5(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5109
335 | Transformer-5(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5110
336 | Old Calcutta-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 181
337 | Old Calcutta-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 182
338 | Old Calcutta-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 183
339 | Old Calcutta-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 184
340 | Old Calcutta-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 185
341 | Old Calcutta-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 186
342 | Old Calcutta-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 187
343 | Old Calcutta-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 188
344 | Old Calcutta-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 189
345 | Old Calcutta-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 190
346 | Old Calcutta-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 191
347 | Old Calcutta-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 192
348 | Old Calcutta-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
349 | Old Calcutta-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13031
350 | Old Calcutta-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13032
351 | Old Calcutta-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
352 | Old Calcutta-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
353 | Old Calcutta-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5111
354 | Old Calcutta-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5112
355 | Old Calcutta-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5113
356 | Old Calcutta-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5114
357 | Old Calcutta-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5115
358 | Old Calcutta-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5116
359 | Old Calcutta-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5117
360 | Old Calcutta-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5118
361 | Old Calcutta-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5119
362 | Old Calcutta-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5120
363 | Old Calcutta-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5121
364 | Old Calcutta-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5122
365 | Old Calcutta-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5123
366 | Old Calcutta-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5124
367 | Old Calcutta-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5125
368 | Old Calcutta-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5126
369 | Old Calcutta-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5127
370 | Old Calcutta-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5128
371 | Old Calcutta-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5129
372 | TSL | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 193
373 | TSL | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 194
374 | TSL | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 195
375 | TSL | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 196
376 | TSL | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 197
377 | TSL | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 198
378 | TSL | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 199
379 | TSL | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 200
380 | TSL | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 201
381 | TSL | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 202
382 | TSL | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 203
383 | TSL | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 204
384 | TSL | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
385 | TSL | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
386 | TSL | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13035
387 | TSL | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
388 | TSL | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
389 | TSL | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5130
390 | TSL | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5131
391 | TSL | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5132
392 | TSL | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5133
393 | TSL | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5134
394 | TSL | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5135
395 | TSL | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5136
396 | TSL | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5137
397 | TSL | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5138
398 | TSL | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5139
399 | TSL | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5140
400 | TSL | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5141
401 | TSL | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5142
402 | TSL | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5143
403 | TSL | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5144
404 | TSL | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5145
405 | TSL | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5146
406 | TSL | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5147
407 | TSL | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5148
408 | KMDA | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 205
409 | KMDA | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 206
410 | KMDA | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 207
411 | KMDA | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 208
412 | KMDA | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 209
413 | KMDA | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 210
414 | KMDA | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 211
415 | KMDA | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 212
416 | KMDA | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 213
417 | KMDA | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 214
418 | KMDA | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 215
419 | KMDA | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 216
420 | KMDA | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
421 | KMDA | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
422 | KMDA | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13038
423 | KMDA | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
424 | KMDA | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
425 | KMDA | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5149
426 | KMDA | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5150
427 | KMDA | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5151
428 | KMDA | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5152
429 | KMDA | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5153
430 | KMDA | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5154
431 | KMDA | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5155
432 | KMDA | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5156
433 | KMDA | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5157
434 | KMDA | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5158
435 | KMDA | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5159
436 | KMDA | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5160
437 | KMDA | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5161
438 | KMDA | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5162
439 | KMDA | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5163
440 | KMDA | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5164
441 | KMDA | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5165
442 | KMDA | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5166
443 | KMDA | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5167
444 | Nilganj | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 217
445 | Nilganj | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 218
446 | Nilganj | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 219
447 | Nilganj | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 220
448 | Nilganj | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 221
449 | Nilganj | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 222
450 | Nilganj | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 223
451 | Nilganj | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 224
452 | Nilganj | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 225
453 | Nilganj | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 226
454 | Nilganj | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 227
455 | Nilganj | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 228
456 | Nilganj | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
457 | Nilganj | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
458 | Nilganj | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13041
459 | Nilganj | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
460 | Nilganj | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
461 | Nilganj | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5168
462 | Nilganj | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5169
463 | Nilganj | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5170
464 | Nilganj | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5171
465 | Nilganj | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5172
466 | Nilganj | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5173
467 | Nilganj | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5174
468 | Nilganj | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5175
469 | Nilganj | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5176
470 | Nilganj | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5177
471 | Nilganj | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5178
472 | Nilganj | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5179
473 | Nilganj | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5180
474 | Nilganj | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5181
475 | Nilganj | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5182
476 | Nilganj | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5183
477 | Nilganj | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5184
478 | Nilganj | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5185
479 | Nilganj | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5186
480 | Dangapara | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 229
481 | Dangapara | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 230
482 | Dangapara | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 231
483 | Dangapara | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 232
484 | Dangapara | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 233
485 | Dangapara | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 234
486 | Dangapara | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 235
487 | Dangapara | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 236
488 | Dangapara | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 237
489 | Dangapara | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 238
490 | Dangapara | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 239
491 | Dangapara | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 240
492 | Dangapara | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
493 | Dangapara | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
494 | Dangapara | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13044
495 | Dangapara | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
496 | Dangapara | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
497 | Dangapara | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5187
498 | Dangapara | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5188
499 | Dangapara | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5189
500 | Dangapara | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5190
501 | Dangapara | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5191
502 | Dangapara | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5192
503 | Dangapara | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5193
504 | Dangapara | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5194
505 | Dangapara | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5195
506 | Dangapara | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5196
507 | Dangapara | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5197
508 | Dangapara | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5198
509 | Dangapara | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5199
510 | Dangapara | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5200
511 | Dangapara | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5201
512 | Dangapara | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5202
513 | Dangapara | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5203
514 | Dangapara | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5204
515 | Dangapara | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5205
516 | Old Calcutta CKT-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 241
517 | Old Calcutta CKT-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 242
518 | Old Calcutta CKT-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 243
519 | Old Calcutta CKT-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 244
520 | Old Calcutta CKT-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 245
521 | Old Calcutta CKT-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 246
522 | Old Calcutta CKT-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 247
523 | Old Calcutta CKT-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 248
524 | Old Calcutta CKT-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 249
525 | Old Calcutta CKT-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 250
526 | Old Calcutta CKT-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 251
527 | Old Calcutta CKT-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 252
528 | Old Calcutta CKT-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
529 | Old Calcutta CKT-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13046
530 | Old Calcutta CKT-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13047
531 | Old Calcutta CKT-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
532 | Old Calcutta CKT-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
533 | Old Calcutta CKT-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5206
534 | Old Calcutta CKT-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5207
535 | Old Calcutta CKT-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5208
536 | Old Calcutta CKT-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5209
537 | Old Calcutta CKT-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5210
538 | Old Calcutta CKT-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5211
539 | Old Calcutta CKT-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5212
540 | Old Calcutta CKT-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5213
541 | Old Calcutta CKT-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5214
542 | Old Calcutta CKT-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5215
543 | Old Calcutta CKT-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5216
544 | Old Calcutta CKT-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5217
545 | Old Calcutta CKT-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5218
546 | Old Calcutta CKT-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5219
547 | Old Calcutta CKT-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5220
548 | Old Calcutta CKT-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5221
549 | Old Calcutta CKT-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5222
550 | Old Calcutta CKT-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5223
551 | Old Calcutta CKT-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5224
552 | Dhania Para | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 253
553 | Dhania Para | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 254
554 | Dhania Para | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 255
555 | Dhania Para | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 256
556 | Dhania Para | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 257
557 | Dhania Para | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 258
558 | Dhania Para | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 259
559 | Dhania Para | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 260
560 | Dhania Para | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 261
561 | Dhania Para | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 262
562 | Dhania Para | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 263
563 | Dhania Para | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 264
564 | Dhania Para | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 265
565 | Dhania Para | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 266
566 | Dhania Para | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
567 | Dhania Para | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
568 | Dhania Para | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
569 | Dhania Para | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
570 | Dhania Para | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
571 | Dhania Para | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5225
572 | Dhania Para | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5226
573 | Dhania Para | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5227
574 | Dhania Para | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5228
575 | Dhania Para | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5229
576 | Dhania Para | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5230
577 | Dhania Para | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5231
578 | Dhania Para | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5232
579 | Dhania Para | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5233
580 | Dhania Para | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5234
581 | Dhania Para | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5235
582 | Dhania Para | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5236
583 | Dhania Para | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5237
584 | Dhania Para | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5238
585 | Dhania Para | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5239
586 | Dhania Para | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5240
587 | Dhania Para | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5241
588 | Incomer-5 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 267
589 | Incomer-5 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 268
590 | Incomer-5 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 269
591 | Incomer-5 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 270
592 | Incomer-5 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 271
593 | Incomer-5 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 272
594 | Incomer-5 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 273
595 | Incomer-5 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 274
596 | Incomer-5 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 275
597 | Incomer-5 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 276
598 | Incomer-5 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 277
599 | Incomer-5 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 278
600 | Incomer-5 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 279
601 | Incomer-5 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
602 | Incomer-5 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
603 | Incomer-5 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
604 | Incomer-5 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13052
605 | Incomer-5 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13053
606 | Incomer-5 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5242
607 | Incomer-5 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5243
608 | Incomer-5 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5244
609 | Incomer-5 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5245
610 | Incomer-5 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5246
611 | Incomer-5 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5247
612 | Incomer-5 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5248
613 | Incomer-5 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5249
614 | Incomer-5 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5250
615 | Incomer-5 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5251
616 | Incomer-5 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5252
617 | Incomer-5 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5253
618 | Incomer-5 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5254
619 | Incomer-5 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5255
620 | Incomer-5 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5256
621 | Incomer-5 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5257
622 | Incomer-5 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5258
623 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 280
624 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 281
625 | Bus Coupler-4 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 282
626 | Bus Coupler-4 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 283
627 | Bus Coupler-4 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 284
628 | Bus Coupler-4 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 285
629 | Bus Coupler-4 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 286
630 | Bus Coupler-4 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 287 |  |  |  | AC CMR to be used
631 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 288
632 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 289
633 | Bus Coupler-4 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10014
634 | Bus Coupler-4 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10014
635 | Harisava | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 290
636 | Harisava | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 291
637 | Harisava | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 292
638 | Harisava | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 293
639 | Harisava | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 294
640 | Harisava | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 295
641 | Harisava | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 296
642 | Harisava | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 297
643 | Harisava | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 298
644 | Harisava | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 299
645 | Harisava | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 300
646 | Harisava | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 301
647 | Harisava | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 302
648 | Harisava | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 303
649 | Harisava | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
650 | Harisava | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
651 | Harisava | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
652 | Harisava | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
653 | Harisava | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
654 | Harisava | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5259
655 | Harisava | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5260
656 | Harisava | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5261
657 | Harisava | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5262
658 | Harisava | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5263
659 | Harisava | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5264
660 | Harisava | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5265
661 | Harisava | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5266
662 | Harisava | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5267
663 | Harisava | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5268
664 | Harisava | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5269
665 | Harisava | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5270
666 | Harisava | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5271
667 | Harisava | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5272
668 | Harisava | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5273
669 | Harisava | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5274
670 | Harisava | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5275
671 | Nandan Nagar | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 304
672 | Nandan Nagar | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 305
673 | Nandan Nagar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 306
674 | Nandan Nagar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 307
675 | Nandan Nagar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 308
676 | Nandan Nagar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 309
677 | Nandan Nagar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 310
678 | Nandan Nagar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 311
679 | Nandan Nagar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 312
680 | Nandan Nagar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 313
681 | Nandan Nagar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 314
682 | Nandan Nagar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 315
683 | Nandan Nagar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 316
684 | Nandan Nagar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 317
685 | Nandan Nagar | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
686 | Nandan Nagar | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
687 | Nandan Nagar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
688 | Nandan Nagar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
689 | Nandan Nagar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
690 | Nandan Nagar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5276
691 | Nandan Nagar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5277
692 | Nandan Nagar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5278
693 | Nandan Nagar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5279
694 | Nandan Nagar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5280
695 | Nandan Nagar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5281
696 | Nandan Nagar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5282
697 | Nandan Nagar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5283
698 | Nandan Nagar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5284
699 | Nandan Nagar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5285
700 | Nandan Nagar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5286
701 | Nandan Nagar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5287
702 | Nandan Nagar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5288
703 | Nandan Nagar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5289
704 | Nandan Nagar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5290
705 | Nandan Nagar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5291
706 | Nandan Nagar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5292
707 | Incomer-4 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 318
708 | Incomer-4 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 319
709 | Incomer-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 320
710 | Incomer-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 321
711 | Incomer-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 322
712 | Incomer-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 323
713 | Incomer-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 324
714 | Incomer-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 325
715 | Incomer-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 326
716 | Incomer-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 327
717 | Incomer-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 328
718 | Incomer-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 329
719 | Incomer-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 330
720 | Incomer-4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
721 | Incomer-4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
722 | Incomer-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
723 | Incomer-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13061
724 | Incomer-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13062
725 | Incomer-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5293
726 | Incomer-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5294
727 | Incomer-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5295
728 | Incomer-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5296
729 | Incomer-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5297
730 | Incomer-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5298
731 | Incomer-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5299
732 | Incomer-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5300
733 | Incomer-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5301
734 | Incomer-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5302
735 | Incomer-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5303
736 | Incomer-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5304
737 | Incomer-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5305
738 | Incomer-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5306
739 | Incomer-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5307
740 | Incomer-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5308
741 | Incomer-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5309
742 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 331
743 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 332
744 | Bus Coupler-3 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 333
745 | Bus Coupler-3 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 334
746 | Bus Coupler-3 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 335
747 | Bus Coupler-3 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 336
748 | Bus Coupler-3 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 337
749 | Bus Coupler-3 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 338 |  |  |  | AC CMR to be used
750 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 339
751 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 340
752 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10018
753 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10018
754 | Pan Para | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 341
755 | Pan Para | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 342
756 | Pan Para | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 343
757 | Pan Para | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 344
758 | Pan Para | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 345
759 | Pan Para | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 346
760 | Pan Para | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 347
761 | Pan Para | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 348
762 | Pan Para | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 349
763 | Pan Para | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 350
764 | Pan Para | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 351
765 | Pan Para | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 352
766 | Pan Para | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 353
767 | Pan Para | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 354
768 | Pan Para | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
769 | Pan Para | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
770 | Pan Para | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
771 | Pan Para | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
772 | Pan Para | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
773 | Pan Para | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5310
774 | Pan Para | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5311
775 | Pan Para | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5312
776 | Pan Para | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5313
777 | Pan Para | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5314
778 | Pan Para | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5315
779 | Pan Para | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5316
780 | Pan Para | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5317
781 | Pan Para | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5318
782 | Pan Para | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5319
783 | Pan Para | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5320
784 | Pan Para | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5321
785 | Pan Para | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5322
786 | Pan Para | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5323
787 | Pan Para | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5324
788 | Pan Para | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5325
789 | Pan Para | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5326
790 | Sadar Bazar | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 355
791 | Sadar Bazar | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 356
792 | Sadar Bazar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 357
793 | Sadar Bazar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 358
794 | Sadar Bazar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 359
795 | Sadar Bazar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 360
796 | Sadar Bazar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 361
797 | Sadar Bazar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 362
798 | Sadar Bazar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 363
799 | Sadar Bazar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 364
800 | Sadar Bazar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 365
801 | Sadar Bazar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 366
802 | Sadar Bazar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 367
803 | Sadar Bazar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 368
804 | Sadar Bazar | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
805 | Sadar Bazar | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
806 | Sadar Bazar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
807 | Sadar Bazar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
808 | Sadar Bazar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
809 | Sadar Bazar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5327
810 | Sadar Bazar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5328
811 | Sadar Bazar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5329
812 | Sadar Bazar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5330
813 | Sadar Bazar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5331
814 | Sadar Bazar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5332
815 | Sadar Bazar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5333
816 | Sadar Bazar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5334
817 | Sadar Bazar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5335
818 | Sadar Bazar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5336
819 | Sadar Bazar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5337
820 | Sadar Bazar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5338
821 | Sadar Bazar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5339
822 | Sadar Bazar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5340
823 | Sadar Bazar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5341
824 | Sadar Bazar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5342
825 | Sadar Bazar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5343
826 | Patulia | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 369
827 | Patulia | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 370
828 | Patulia | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 371
829 | Patulia | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 372
830 | Patulia | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 373
831 | Patulia | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 374
832 | Patulia | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 375
833 | Patulia | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 376
834 | Patulia | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 377
835 | Patulia | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 378
836 | Patulia | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 379
837 | Patulia | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 380
838 | Patulia | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 381
839 | Patulia | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 382
840 | Patulia | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
841 | Patulia | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
842 | Patulia | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
843 | Patulia | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
844 | Patulia | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
845 | Patulia | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5344
846 | Patulia | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5345
847 | Patulia | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5346
848 | Patulia | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5347
849 | Patulia | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5348
850 | Patulia | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5349
851 | Patulia | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5350
852 | Patulia | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5351
853 | Patulia | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5352
854 | Patulia | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5353
855 | Patulia | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5354
856 | Patulia | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5355
857 | Patulia | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5356
858 | Patulia | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5357
859 | Patulia | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5358
860 | Patulia | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5359
861 | Patulia | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5360
862 | Incomer-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 383
863 | Incomer-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 384
864 | Incomer-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 385
865 | Incomer-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 386
866 | Incomer-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 387
867 | Incomer-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 388
868 | Incomer-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 389
869 | Incomer-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 390
870 | Incomer-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 391
871 | Incomer-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 392
872 | Incomer-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 393
873 | Incomer-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 394
874 | Incomer-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 395
875 | Incomer-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
876 | Incomer-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
877 | Incomer-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
878 | Incomer-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13073
879 | Incomer-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13074
880 | Incomer-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5361
881 | Incomer-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5362
882 | Incomer-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5363
883 | Incomer-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5364
884 | Incomer-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5365
885 | Incomer-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5366
886 | Incomer-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5367
887 | Incomer-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5368
888 | Incomer-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5369
889 | Incomer-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5370
890 | Incomer-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5371
891 | Incomer-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5372
892 | Incomer-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5373
893 | Incomer-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5374
894 | Incomer-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5375
895 | Incomer-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5376
896 | Incomer-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5377
897 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 396
898 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 397
899 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 398
900 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 399
901 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 400
902 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 401
903 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 402
904 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 403 |  |  |  | AC CMR to be used
905 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 404
906 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 405
907 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10023
908 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10023
909 | Ananda Puri | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 406
910 | Ananda Puri | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 407
911 | Ananda Puri | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 408
912 | Ananda Puri | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 409
913 | Ananda Puri | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 410
914 | Ananda Puri | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 411
915 | Ananda Puri | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 412
916 | Ananda Puri | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 413
917 | Ananda Puri | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 414
918 | Ananda Puri | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 415
919 | Ananda Puri | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 416
920 | Ananda Puri | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 417
921 | Ananda Puri | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 418
922 | Ananda Puri | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 419
923 | Ananda Puri | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
924 | Ananda Puri | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
925 | Ananda Puri | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
926 | Ananda Puri | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13076
927 | Ananda Puri | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13077
928 | Ananda Puri | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5378
929 | Ananda Puri | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5379
930 | Ananda Puri | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5380
931 | Ananda Puri | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5381
932 | Ananda Puri | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5382
933 | Ananda Puri | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5383
934 | Ananda Puri | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5384
935 | Ananda Puri | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5385
936 | Ananda Puri | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5386
937 | Ananda Puri | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5387
938 | Ananda Puri | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5388
939 | Ananda Puri | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5389
940 | Ananda Puri | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5390
941 | Ananda Puri | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5391
942 | Ananda Puri | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5392
943 | Ananda Puri | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5393
944 | Ananda Puri | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5394
945 | EMCO | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 420
946 | EMCO | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 421
947 | EMCO | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 422
948 | EMCO | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 423
949 | EMCO | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 424
950 | EMCO | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 425
951 | EMCO | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 426
952 | EMCO | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 427
953 | EMCO | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 428
954 | EMCO | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 429
955 | EMCO | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 430
956 | EMCO | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 431
957 | EMCO | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 432
958 | EMCO | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 433
959 | EMCO | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10025
960 | EMCO | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10025
961 | EMCO | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
962 | EMCO | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13079
963 | EMCO | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13080
964 | EMCO | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5395
965 | EMCO | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5396
966 | EMCO | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5397
967 | EMCO | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5398
968 | EMCO | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5399
969 | EMCO | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5400
970 | EMCO | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5401
971 | EMCO | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5402
972 | EMCO | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5403
973 | EMCO | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5404
974 | EMCO | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5405
975 | EMCO | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5406
976 | EMCO | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5407
977 | EMCO | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5408
978 | EMCO | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5409
979 | EMCO | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5410
980 | EMCO | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5411
981 | Beltala | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 434
982 | Beltala | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 435
983 | Beltala | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 436
984 | Beltala | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 437
985 | Beltala | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 438
986 | Beltala | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 439
987 | Beltala | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 440
988 | Beltala | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 441
989 | Beltala | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 442
990 | Beltala | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 443
991 | Beltala | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 444
992 | Beltala | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 445
993 | Beltala | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 446
994 | Beltala | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 447
995 | Beltala | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
996 | Beltala | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
997 | Beltala | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
998 | Beltala | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13082
999 | Beltala | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13083
1000 | Beltala | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5412
1001 | Beltala | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5413
1002 | Beltala | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5414
1003 | Beltala | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5415
1004 | Beltala | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5416
1005 | Beltala | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5417
1006 | Beltala | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5418
1007 | Beltala | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5419
1008 | Beltala | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5420
1009 | Beltala | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5421
1010 | Beltala | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5422
1011 | Beltala | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5423
1012 | Beltala | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5424
1013 | Beltala | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5425
1014 | Beltala | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5426
1015 | Beltala | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5427
1016 | Beltala | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5428
1017 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 448
1018 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 449
1019 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 450
1020 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 451
1021 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 452
1022 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 453
1023 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 454
1024 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 455 |  |  |  | AC CMR to be used
1025 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 456
1026 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 457
1027 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10027
1028 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10027
1029 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 458
1030 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 459
1031 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 460
1032 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 461
1033 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 462
1034 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 463
1035 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 464
1036 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 465
1037 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 466
1038 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 467
1039 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 468
1040 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 469
1041 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 470
1042 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10028
1043 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10028
1044 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1045 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1046 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13086
1047 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5429
1048 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5430
1049 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5431
1050 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5432
1051 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5433
1052 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5434
1053 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5435
1054 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5436
1055 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5437
1056 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5438
1057 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5439
1058 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5440
1059 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5441
1060 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5442
1061 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5443
1062 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5444
1063 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5445
1064 | Talpukur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 471
1065 | Talpukur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 472
1066 | Talpukur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 473
1067 | Talpukur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 474
1068 | Talpukur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 475
1069 | Talpukur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 476
1070 | Talpukur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 477
1071 | Talpukur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 478
1072 | Talpukur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 479
1073 | Talpukur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 480
1074 | Talpukur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 481
1075 | Talpukur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 482
1076 | Talpukur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 483
1077 | Talpukur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 484
1078 | Talpukur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10029
1079 | Talpukur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10029
1080 | Talpukur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1081 | Talpukur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1082 | Talpukur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13089
1083 | Talpukur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5446
1084 | Talpukur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5447
1085 | Talpukur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5448
1086 | Talpukur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5449
1087 | Talpukur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5450
1088 | Talpukur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5451
1089 | Talpukur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5452
1090 | Talpukur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5453
1091 | Talpukur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5454
1092 | Talpukur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5455
1093 | Talpukur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5456
1094 | Talpukur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5457
1095 | Talpukur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5458
1096 | Talpukur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5459
1097 | Talpukur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5460
1098 | Talpukur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5461
1099 | Talpukur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5462
1100 | Britania | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 485
1101 | Britania | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 486
1102 | Britania | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 487
1103 | Britania | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 488
1104 | Britania | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 489
1105 | Britania | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 490
1106 | Britania | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 491
1107 | Britania | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 492
1108 | Britania | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 493
1109 | Britania | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 494
1110 | Britania | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 495
1111 | Britania | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 496
1112 | Britania | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 497
1113 | Britania | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 498
1114 | Britania | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10030
1115 | Britania | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10030
1116 | Britania | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1117 | Britania | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1118 | Britania | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13092
1119 | Britania | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5463
1120 | Britania | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5464
1121 | Britania | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5465
1122 | Britania | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5466
1123 | Britania | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5467
1124 | Britania | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5468
1125 | Britania | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5469
1126 | Britania | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5470
1127 | Britania | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5471
1128 | Britania | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5472
1129 | Britania | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5473
1130 | Britania | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5474
1131 | Britania | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5475
1132 | Britania | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5476
1133 | Britania | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5477
1134 | Britania | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5478
1135 | Britania | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5479
1136 | GC Road | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 499
1137 | GC Road | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 500
1138 | GC Road | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 501
1139 | GC Road | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 502
1140 | GC Road | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 503
1141 | GC Road | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 504
1142 | GC Road | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 505
1143 | GC Road | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 506
1144 | GC Road | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 507
1145 | GC Road | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 508
1146 | GC Road | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 509
1147 | GC Road | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 510
1148 | GC Road | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 511
1149 | GC Road | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 512
1150 | GC Road | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10031
1151 | GC Road | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10031
1152 | GC Road | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13093
1153 | GC Road | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13094
1154 | GC Road | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13095
1155 | GC Road | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5480
1156 | GC Road | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5481
1157 | GC Road | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5482
1158 | GC Road | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5483
1159 | GC Road | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5484
1160 | GC Road | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5485
1161 | GC Road | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5486
1162 | GC Road | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5487
1163 | GC Road | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5488
1164 | GC Road | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5489
1165 | GC Road | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5490
1166 | GC Road | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5491
1167 | GC Road | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5492
1168 | GC Road | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5493
1169 | GC Road | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5494
1170 | GC Road | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5495
1171 | GC Road | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5496
1172 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 513
1173 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 514
1174 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 515
1175 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 516
1176 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 517
1177 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 518
1178 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 519
1179 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 520
1180 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 521
1181 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 522
1182 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 523
1183 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 524
1184 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 525
1185 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10032
1186 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10032
1187 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13096
1188 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13097
1189 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13098
1190 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5497
1191 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5498
1192 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5499
1193 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5500
1194 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5501
1195 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5502
1196 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5503
1197 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5504
1198 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5505
1199 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5506
1200 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5507
1201 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5508
1202 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5509
1203 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5510
1204 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5511
1205 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5512
1206 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5513
1207 | Future Spare O/G-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 526
1208 | Future Spare O/G-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 527
1209 | Future Spare O/G-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 528
1210 | Future Spare O/G-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 529
1211 | Future Spare O/G-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 530
1212 | Future Spare O/G-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 531
1213 | Future Spare O/G-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 532
1214 | Future Spare O/G-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 533
1215 | Future Spare O/G-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 534
1216 | Future Spare O/G-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 535
1217 | Future Spare O/G-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 536
1218 | Future Spare O/G-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 537
1219 | Future Spare O/G-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 538
1220 | Future Spare O/G-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 539
1221 | Future Spare O/G-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10033
1222 | Future Spare O/G-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10033
1223 | Future Spare O/G-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13099
1224 | Future Spare O/G-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13100
1225 | Future Spare O/G-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13101
1226 | Future Spare O/G-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5514
1227 | Future Spare O/G-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5515
1228 | Future Spare O/G-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5516
1229 | Future Spare O/G-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5517
1230 | Future Spare O/G-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5518
1231 | Future Spare O/G-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5519
1232 | Future Spare O/G-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5520
1233 | Future Spare O/G-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5521
1234 | Future Spare O/G-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5522
1235 | Future Spare O/G-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5523
1236 | Future Spare O/G-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5524
1237 | Future Spare O/G-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5525
1238 | Future Spare O/G-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5526
1239 | Future Spare O/G-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5527
1240 | Future Spare O/G-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5528
1241 | Future Spare O/G-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5529
1242 | Future Spare O/G-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5530
1243 | Future Spare O/G-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 540
1244 | Future Spare O/G-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 541
1245 | Future Spare O/G-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 542
1246 | Future Spare O/G-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 543
1247 | Future Spare O/G-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 544
1248 | Future Spare O/G-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 545
1249 | Future Spare O/G-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 546
1250 | Future Spare O/G-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 547
1251 | Future Spare O/G-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 548
1252 | Future Spare O/G-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 549
1253 | Future Spare O/G-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 550
1254 | Future Spare O/G-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 551
1255 | Future Spare O/G-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 552
1256 | Future Spare O/G-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 553
1257 | Future Spare O/G-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10034
1258 | Future Spare O/G-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10034
1259 | Future Spare O/G-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13102
1260 | Future Spare O/G-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13103
1261 | Future Spare O/G-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13104
1262 | Future Spare O/G-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5531
1263 | Future Spare O/G-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5532
1264 | Future Spare O/G-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5533
1265 | Future Spare O/G-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5534
1266 | Future Spare O/G-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5535
1267 | Future Spare O/G-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5536
1268 | Future Spare O/G-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5537
1269 | Future Spare O/G-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5538
1270 | Future Spare O/G-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5539
1271 | Future Spare O/G-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5540
1272 | Future Spare O/G-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5541
1273 | Future Spare O/G-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5542
1274 | Future Spare O/G-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5543
1275 | Future Spare O/G-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5544
1276 | Future Spare O/G-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5545
1277 | Future Spare O/G-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5546
1278 | Future Spare O/G-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5547
1279 | Future Spare O/G-3 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 554
1280 | Future Spare O/G-3 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 555
1281 | Future Spare O/G-3 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 556
1282 | Future Spare O/G-3 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 557
1283 | Future Spare O/G-3 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 558
1284 | Future Spare O/G-3 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 559
1285 | Future Spare O/G-3 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 560
1286 | Future Spare O/G-3 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 561
1287 | Future Spare O/G-3 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 562
1288 | Future Spare O/G-3 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 563
1289 | Future Spare O/G-3 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 564
1290 | Future Spare O/G-3 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 565
1291 | Future Spare O/G-3 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 566
1292 | Future Spare O/G-3 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 567
1293 | Future Spare O/G-3 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10035
1294 | Future Spare O/G-3 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10035
1295 | Future Spare O/G-3 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13105
1296 | Future Spare O/G-3 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13106
1297 | Future Spare O/G-3 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13107
1298 | Future Spare O/G-3 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5548
1299 | Future Spare O/G-3 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5549
1300 | Future Spare O/G-3 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5550
1301 | Future Spare O/G-3 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5551
1302 | Future Spare O/G-3 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5552
1303 | Future Spare O/G-3 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5553
1304 | Future Spare O/G-3 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5554
1305 | Future Spare O/G-3 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5555
1306 | Future Spare O/G-3 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5556
1307 | Future Spare O/G-3 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5557
1308 | Future Spare O/G-3 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5558
1309 | Future Spare O/G-3 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5559
1310 | Future Spare O/G-3 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5560
1311 | Future Spare O/G-3 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5561
1312 | Future Spare O/G-3 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5562
1313 | Future Spare O/G-3 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5563
1314 | Future Spare O/G-3 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5564
1315 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5565
1316 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5566
1317 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5567
1318 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5568
1319 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5569
1320 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5570
1321 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5571