## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | DUMMY CB | 3000
23 | Sub-Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | DUMMY CB | 10000
24 | Sub-Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer-3 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer-3 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | M5 Inter connector | 33kV | I/C + Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 112
209 | M5 Inter connector | 33kV | I/C + Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 113
210 | M5 Inter connector | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 114
211 | M5 Inter connector | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 115
212 | M5 Inter connector | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 116
213 | M5 Inter connector | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 117
214 | M5 Inter connector | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 118
215 | M5 Inter connector | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 119
216 | M5 Inter connector | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 120
217 | M5 Inter connector | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 121
218 | M5 Inter connector | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 122
219 | M5 Inter connector | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 123
220 | M5 Inter connector | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
221 | M5 Inter connector | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13019
222 | M5 Inter connector | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13020
223 | M5 Inter connector | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10004
224 | M5 Inter connector | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10004
225 | M5 Inter connector | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5068
226 | M5 Inter connector | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5069
227 | M5 Inter connector | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5070
228 | M5 Inter connector | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5071
229 | M5 Inter connector | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5072
230 | M5 Inter connector | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5073
231 | M5 Inter connector | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5074
232 | M5 Inter connector | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5075
233 | M5 Inter connector | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5076
234 | M5 Inter connector | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5077
235 | M5 Inter connector | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5078
236 | M5 Inter connector | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5079
237 | M5 Inter connector | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5080
238 | M5 Inter connector | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5081
239 | M5 Inter connector | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5082
240 | M5 Inter connector | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
241 | M5 Inter connector | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
242 | M5 Inter connector | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5085
243 | M5 Inter connector | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5086
244 | New town inter connector | 33kV | I/C + Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 124
245 | New town inter connector | 33kV | I/C + Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 125
246 | New town inter connector | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 126
247 | New town inter connector | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 127
248 | New town inter connector | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 128
249 | New town inter connector | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 129
250 | New town inter connector | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 130
251 | New town inter connector | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 131
252 | New town inter connector | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 132
253 | New town inter connector | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 133
254 | New town inter connector | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 134
255 | New town inter connector | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 135
256 | New town inter connector | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
257 | New town inter connector | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13022
258 | New town inter connector | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13023
259 | New town inter connector | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
260 | New town inter connector | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
261 | New town inter connector | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5087
262 | New town inter connector | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5088
263 | New town inter connector | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5089
264 | New town inter connector | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5090
265 | New town inter connector | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5091
266 | New town inter connector | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5092
267 | New town inter connector | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5093
268 | New town inter connector | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5094
269 | New town inter connector | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5095
270 | New town inter connector | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5096
271 | New town inter connector | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5097
272 | New town inter connector | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5098
273 | New town inter connector | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5099
274 | New town inter connector | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5100
275 | New town inter connector | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5101
276 | New town inter connector | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5102
277 | New town inter connector | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5103
278 | New town inter connector | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5104
279 | New town inter connector | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5105
280 | Incoming-1 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 136
281 | Incoming-1 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 137
282 | Incoming-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 138
283 | Incoming-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 139
284 | Incoming-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 140
285 | Incoming-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 141
286 | Incoming-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 142
287 | Incoming-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 143
288 | Incoming-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 144
289 | Incoming-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 145
290 | Incoming-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 146
291 | Incoming-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 147
292 | Incoming-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
293 | Incoming-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
294 | Incoming-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
295 | Incoming-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
296 | Incoming-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
297 | Incoming-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5106
298 | Incoming-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5107
299 | Incoming-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5108
300 | Incoming-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5109
301 | Incoming-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5110
302 | Incoming-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5111
303 | Incoming-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5112
304 | Incoming-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5113
305 | Incoming-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5114
306 | Incoming-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5115
307 | Incoming-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5116
308 | Incoming-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5117
309 | Incoming-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5118
310 | Incoming-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5119
311 | Incoming-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5120
312 | Incoming-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5121
313 | Incoming-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5122
314 | Incoming-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5123
315 | Incoming-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5124
316 | Incoming-2 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 148
317 | Incoming-2 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 149
318 | Incoming-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 150
319 | Incoming-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 151
320 | Incoming-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 152
321 | Incoming-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 153
322 | Incoming-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 154
323 | Incoming-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 155
324 | Incoming-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 156
325 | Incoming-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 157
326 | Incoming-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 158
327 | Incoming-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 159
328 | Incoming-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
329 | Incoming-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
330 | Incoming-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13029
331 | Incoming-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
332 | Incoming-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
333 | Incoming-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5125
334 | Incoming-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5126
335 | Incoming-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5127
336 | Incoming-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5128
337 | Incoming-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5129
338 | Incoming-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5130
339 | Incoming-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5131
340 | Incoming-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5132
341 | Incoming-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5133
342 | Incoming-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5134
343 | Incoming-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5135
344 | Incoming-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5136
345 | Incoming-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5137
346 | Incoming-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5138
347 | Incoming-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5139
348 | Incoming-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5140
349 | Incoming-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5141
350 | Incoming-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5142
351 | Incoming-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5143
352 | Srijan | 33kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 160
353 | Srijan | 33kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 161
354 | Srijan | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 162
355 | Srijan | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 163
356 | Srijan | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 164
357 | Srijan | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 165
358 | Srijan | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 166
359 | Srijan | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 167
360 | Srijan | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 168
361 | Srijan | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 169
362 | Srijan | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 170
363 | Srijan | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 171
364 | Srijan | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
365 | Srijan | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
366 | Srijan | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13032
367 | Srijan | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
368 | Srijan | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
369 | Srijan | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5144
370 | Srijan | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5145
371 | Srijan | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5146
372 | Srijan | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5147
373 | Srijan | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5148
374 | Srijan | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5149
375 | Srijan | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5150
376 | Srijan | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5151
377 | Srijan | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5152
378 | Srijan | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5153
379 | Srijan | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5154
380 | Srijan | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5155
381 | Srijan | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5156
382 | Srijan | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5157
383 | Srijan | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5158
384 | Srijan | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5159
385 | Srijan | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5160
386 | Srijan | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5161
387 | Srijan | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5162
388 | Incomer-1 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 172
389 | Incomer-1 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 173
390 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 174
391 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 175
392 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 176
393 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 177
394 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 178
395 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 179
396 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 180
397 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 181
398 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 182
399 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 183
400 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 184
401 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
402 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
403 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
404 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13034
405 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13035
406 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5163
407 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5164
408 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5165
409 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5166
410 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5167
411 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5168
412 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5169
413 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5170
414 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5171
415 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5172
416 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5173
417 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5174
418 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5175
419 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5176
420 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5177
421 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5178
422 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5179
423 | ITT-1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 185
424 | ITT-1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 186
425 | ITT-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 187
426 | ITT-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 188
427 | ITT-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 189
428 | ITT-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 190
429 | ITT-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 191
430 | ITT-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 192
431 | ITT-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 193
432 | ITT-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 194
433 | ITT-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 195
434 | ITT-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 196
435 | ITT-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 197
436 | ITT-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 198
437 | ITT-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
438 | ITT-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
439 | ITT-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
440 | ITT-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
441 | ITT-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
442 | ITT-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5180
443 | ITT-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5181
444 | ITT-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5182
445 | ITT-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5183
446 | ITT-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5184
447 | ITT-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5185
448 | ITT-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5186
449 | ITT-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5187
450 | ITT-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5188
451 | ITT-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5189
452 | ITT-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5190
453 | ITT-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5191
454 | ITT-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5192
455 | ITT-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5193
456 | ITT-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5194
457 | ITT-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5195
458 | ITT-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5196
459 | SS-2 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 199
460 | SS-2 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 200
461 | SS-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 201
462 | SS-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 202
463 | SS-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 203
464 | SS-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 204
465 | SS-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 205
466 | SS-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 206
467 | SS-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 207
468 | SS-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 208
469 | SS-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 209
470 | SS-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 210
471 | SS-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 211
472 | SS-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 212
473 | SS-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
474 | SS-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
475 | SS-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
476 | SS-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
477 | SS-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
478 | SS-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5197
479 | SS-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5198
480 | SS-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5199
481 | SS-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5200
482 | SS-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5201
483 | SS-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5202
484 | SS-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5203
485 | SS-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5204
486 | SS-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5205
487 | SS-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5206
488 | SS-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5207
489 | SS-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5208
490 | SS-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5209
491 | SS-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5210
492 | SS-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5211
493 | SS-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5212
494 | SS-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5213
495 | Godrej | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 213
496 | Godrej | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 214
497 | Godrej | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 215
498 | Godrej | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 216
499 | Godrej | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 217
500 | Godrej | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 218
501 | Godrej | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 219
502 | Godrej | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 220
503 | Godrej | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 221
504 | Godrej | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 222
505 | Godrej | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 223
506 | Godrej | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 224
507 | Godrej | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 225
508 | Godrej | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 226
509 | Godrej | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
510 | Godrej | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
511 | Godrej | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
512 | Godrej | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
513 | Godrej | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
514 | Godrej | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5214
515 | Godrej | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5215
516 | Godrej | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5216
517 | Godrej | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5217
518 | Godrej | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5218
519 | Godrej | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5219
520 | Godrej | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5220
521 | Godrej | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5221
522 | Godrej | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5222
523 | Godrej | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5223
524 | Godrej | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5224
525 | Godrej | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5225
526 | Godrej | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5226
527 | Godrej | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5227
528 | Godrej | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5228
529 | Godrej | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5229
530 | Godrej | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5230
531 | Bus coupler-1 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 227
532 | Bus coupler-1 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 228
533 | Bus coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 229
534 | Bus coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 230
535 | Bus coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 231
536 | Bus coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 232
537 | Bus coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 233
538 | Bus coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 234 |  |  |  | AC CMR to be used
539 | Bus coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 235
540 | Bus coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 236
541 | Bus coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10013
542 | Bus coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10013
543 | Incomer-2 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 237
544 | Incomer-2 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 238
545 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 239
546 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 240
547 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 241
548 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 242
549 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 243
550 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 244
551 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 245
552 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 246
553 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 247
554 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 248
555 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 249
556 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
557 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
558 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
559 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13046
560 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13047
561 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5231
562 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5232
563 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5233
564 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5234
565 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5235
566 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5236
567 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5237
568 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5238
569 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5239
570 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5240
571 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5241
572 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5242
573 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5243
574 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5244
575 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5245
576 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5246
577 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5247
578 | SS-3 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 250
579 | SS-3 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 251
580 | SS-3 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 252
581 | SS-3 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 253
582 | SS-3 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 254
583 | SS-3 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 255
584 | SS-3 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 256
585 | SS-3 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 257
586 | SS-3 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 258
587 | SS-3 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 259
588 | SS-3 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 260
589 | SS-3 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 261
590 | SS-3 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 262
591 | SS-3 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 263
592 | SS-3 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
593 | SS-3 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
594 | SS-3 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
595 | SS-3 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
596 | SS-3 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
597 | SS-3 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5248
598 | SS-3 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5249
599 | SS-3 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5250
600 | SS-3 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5251
601 | SS-3 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5252
602 | SS-3 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5253
603 | SS-3 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5254
604 | SS-3 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5255
605 | SS-3 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5256
606 | SS-3 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5257
607 | SS-3 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5258
608 | SS-3 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5259
609 | SS-3 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5260
610 | SS-3 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5261
611 | SS-3 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5262
612 | SS-3 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5263
613 | SS-3 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5264
614 | TCS-1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 264
615 | TCS-1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 265
616 | TCS-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 266
617 | TCS-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 267
618 | TCS-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 268
619 | TCS-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 269
620 | TCS-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 270
621 | TCS-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 271
622 | TCS-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 272
623 | TCS-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 273
624 | TCS-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 274
625 | TCS-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 275
626 | TCS-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 276
627 | TCS-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 277
628 | TCS-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
629 | TCS-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
630 | TCS-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
631 | TCS-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
632 | TCS-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
633 | TCS-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5265
634 | TCS-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5266
635 | TCS-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5267
636 | TCS-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5268
637 | TCS-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5269
638 | TCS-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5270
639 | TCS-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5271
640 | TCS-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5272
641 | TCS-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5273
642 | TCS-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5274
643 | TCS-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5275
644 | TCS-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5276
645 | TCS-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5277
646 | TCS-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5278
647 | TCS-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5279
648 | TCS-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5280
649 | TCS-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5281
650 | Nayapatty | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 278
651 | Nayapatty | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 279
652 | Nayapatty | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 280
653 | Nayapatty | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 281
654 | Nayapatty | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 282
655 | Nayapatty | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 283
656 | Nayapatty | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 284
657 | Nayapatty | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 285
658 | Nayapatty | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 286
659 | Nayapatty | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 287
660 | Nayapatty | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 288
661 | Nayapatty | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 289
662 | Nayapatty | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 290
663 | Nayapatty | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 291
664 | Nayapatty | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
665 | Nayapatty | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
666 | Nayapatty | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
667 | Nayapatty | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
668 | Nayapatty | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
669 | Nayapatty | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5282
670 | Nayapatty | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5283
671 | Nayapatty | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5284
672 | Nayapatty | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5285
673 | Nayapatty | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5286
674 | Nayapatty | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5287
675 | Nayapatty | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5288
676 | Nayapatty | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5289
677 | Nayapatty | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5290
678 | Nayapatty | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5291
679 | Nayapatty | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5292
680 | Nayapatty | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5293
681 | Nayapatty | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5294
682 | Nayapatty | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5295
683 | Nayapatty | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5296
684 | Nayapatty | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5297
685 | Nayapatty | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5298
686 | Germinda | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 292
687 | Germinda | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 293
688 | Germinda | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 294
689 | Germinda | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 295
690 | Germinda | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 296
691 | Germinda | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 297
692 | Germinda | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 298
693 | Germinda | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 299
694 | Germinda | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 300
695 | Germinda | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 301
696 | Germinda | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 302
697 | Germinda | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 303
698 | Germinda | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 304
699 | Germinda | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 305
700 | Germinda | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
701 | Germinda | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
702 | Germinda | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
703 | Germinda | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
704 | Germinda | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
705 | Germinda | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5299
706 | Germinda | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5300
707 | Germinda | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5301
708 | Germinda | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5302
709 | Germinda | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5303
710 | Germinda | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5304
711 | Germinda | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5305
712 | Germinda | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5306
713 | Germinda | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5307
714 | Germinda | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5308
715 | Germinda | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5309
716 | Germinda | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5310
717 | Germinda | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5311
718 | Germinda | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5312
719 | Germinda | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5313
720 | Germinda | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5314
721 | Germinda | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5315
722 | SB Stichers | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 306
723 | SB Stichers | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 307
724 | SB Stichers | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 308
725 | SB Stichers | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 309
726 | SB Stichers | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 310
727 | SB Stichers | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 311
728 | SB Stichers | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 312
729 | SB Stichers | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 313
730 | SB Stichers | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 314
731 | SB Stichers | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 315
732 | SB Stichers | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 316
733 | SB Stichers | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 317
734 | SB Stichers | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 318
735 | SB Stichers | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 319
736 | SB Stichers | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
737 | SB Stichers | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
738 | SB Stichers | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
739 | SB Stichers | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
740 | SB Stichers | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
741 | SB Stichers | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5316
742 | SB Stichers | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5317
743 | SB Stichers | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5318
744 | SB Stichers | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5319
745 | SB Stichers | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5320
746 | SB Stichers | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5321
747 | SB Stichers | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5322
748 | SB Stichers | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5323
749 | SB Stichers | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5324
750 | SB Stichers | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5325
751 | SB Stichers | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5326
752 | SB Stichers | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5327
753 | SB Stichers | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5328
754 | SB Stichers | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5329
755 | SB Stichers | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5330
756 | SB Stichers | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5331
757 | SB Stichers | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5332
758 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 320
759 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 321
760 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 322
761 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 323
762 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 324
763 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 325
764 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 326
765 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 327 |  |  |  | AC CMR to be used
766 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 328
767 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 329
768 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10020
769 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10020
770 | Incomer-3 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 330
771 | Incomer-3 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 331
772 | Incomer-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 332
773 | Incomer-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 333
774 | Incomer-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 334
775 | Incomer-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 335
776 | Incomer-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 336
777 | Incomer-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 337
778 | Incomer-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 338
779 | Incomer-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 339
780 | Incomer-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 340
781 | Incomer-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 341
782 | Incomer-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 342
783 | Incomer-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
784 | Incomer-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
785 | Incomer-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
786 | Incomer-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13064
787 | Incomer-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13065
788 | Incomer-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5333
789 | Incomer-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5334
790 | Incomer-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5335
791 | Incomer-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5336
792 | Incomer-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5337
793 | Incomer-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5338
794 | Incomer-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5339
795 | Incomer-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5340
796 | Incomer-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5341
797 | Incomer-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5342
798 | Incomer-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5343
799 | Incomer-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5344
800 | Incomer-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5345
801 | Incomer-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5346
802 | Incomer-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5347
803 | Incomer-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5348
804 | Incomer-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5349
805 | Imagine tech park-1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 343
806 | Imagine tech park-1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 344
807 | Imagine tech park-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 345
808 | Imagine tech park-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 346
809 | Imagine tech park-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 347
810 | Imagine tech park-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 348
811 | Imagine tech park-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 349
812 | Imagine tech park-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 350
813 | Imagine tech park-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 351
814 | Imagine tech park-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 352
815 | Imagine tech park-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 353
816 | Imagine tech park-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 354
817 | Imagine tech park-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 355
818 | Imagine tech park-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 356
819 | Imagine tech park-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
820 | Imagine tech park-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
821 | Imagine tech park-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
822 | Imagine tech park-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
823 | Imagine tech park-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
824 | Imagine tech park-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5350
825 | Imagine tech park-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5351
826 | Imagine tech park-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5352
827 | Imagine tech park-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5353
828 | Imagine tech park-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5354
829 | Imagine tech park-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5355
830 | Imagine tech park-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5356
831 | Imagine tech park-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5357
832 | Imagine tech park-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5358
833 | Imagine tech park-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5359
834 | Imagine tech park-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5360
835 | Imagine tech park-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5361
836 | Imagine tech park-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5362
837 | Imagine tech park-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5363
838 | Imagine tech park-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5364
839 | Imagine tech park-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5365
840 | Imagine tech park-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5366
841 | M5 Mahisbathan inter connector | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 357
842 | M5 Mahisbathan inter connector | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 358
843 | M5 Mahisbathan inter connector | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 359
844 | M5 Mahisbathan inter connector | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 360
845 | M5 Mahisbathan inter connector | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 361
846 | M5 Mahisbathan inter connector | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 362
847 | M5 Mahisbathan inter connector | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 363
848 | M5 Mahisbathan inter connector | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 364
849 | M5 Mahisbathan inter connector | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 365
850 | M5 Mahisbathan inter connector | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 366
851 | M5 Mahisbathan inter connector | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 367
852 | M5 Mahisbathan inter connector | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 368
853 | M5 Mahisbathan inter connector | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 369
854 | M5 Mahisbathan inter connector | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
855 | M5 Mahisbathan inter connector | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
856 | M5 Mahisbathan inter connector | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
857 | M5 Mahisbathan inter connector | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13070
858 | M5 Mahisbathan inter connector | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13071
859 | M5 Mahisbathan inter connector | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5367
860 | M5 Mahisbathan inter connector | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5368
861 | M5 Mahisbathan inter connector | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5369
862 | M5 Mahisbathan inter connector | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5370
863 | M5 Mahisbathan inter connector | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5371
864 | M5 Mahisbathan inter connector | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5372
865 | M5 Mahisbathan inter connector | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5373
866 | M5 Mahisbathan inter connector | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5374
867 | M5 Mahisbathan inter connector | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5375
868 | M5 Mahisbathan inter connector | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5376
869 | M5 Mahisbathan inter connector | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5377
870 | M5 Mahisbathan inter connector | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5378
871 | M5 Mahisbathan inter connector | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5379
872 | M5 Mahisbathan inter connector | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5380
873 | M5 Mahisbathan inter connector | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5381
874 | M5 Mahisbathan inter connector | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5382
875 | M5 Mahisbathan inter connector | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5383
876 | SDF | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 370
877 | SDF | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 371
878 | SDF | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 372
879 | SDF | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 373
880 | SDF | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 374
881 | SDF | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 375
882 | SDF | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 376
883 | SDF | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 377
884 | SDF | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 378
885 | SDF | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 379
886 | SDF | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 380
887 | SDF | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 381
888 | SDF | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 382
889 | SDF | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 383
890 | SDF | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
891 | SDF | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
892 | SDF | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
893 | SDF | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
894 | SDF | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
895 | SDF | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5384
896 | SDF | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5385
897 | SDF | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5386
898 | SDF | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5387
899 | SDF | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5388
900 | SDF | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5389
901 | SDF | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5390
902 | SDF | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5391
903 | SDF | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5392
904 | SDF | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5393
905 | SDF | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5394
906 | SDF | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5395
907 | SDF | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5396
908 | SDF | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5397
909 | SDF | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5398
910 | SDF | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5399
911 | SDF | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5400
912 | Wipro | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 384
913 | Wipro | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 385
914 | Wipro | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 386
915 | Wipro | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 387
916 | Wipro | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 388
917 | Wipro | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 389
918 | Wipro | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 390
919 | Wipro | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 391
920 | Wipro | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 392
921 | Wipro | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 393
922 | Wipro | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 394
923 | Wipro | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 395
924 | Wipro | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 396
925 | Wipro | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 397
926 | Wipro | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10025
927 | Wipro | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10025
928 | Wipro | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
929 | Wipro | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13076
930 | Wipro | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13077
931 | Wipro | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5401
932 | Wipro | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5402
933 | Wipro | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5403
934 | Wipro | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5404
935 | Wipro | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5405
936 | Wipro | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5406
937 | Wipro | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5407
938 | Wipro | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5408
939 | Wipro | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5409
940 | Wipro | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5410
941 | Wipro | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5411
942 | Wipro | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5412
943 | Wipro | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5413
944 | Wipro | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5414
945 | Wipro | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5415
946 | Wipro | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5416
947 | Wipro | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5417
948 | Super intendence | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 398
949 | Super intendence | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 399
950 | Super intendence | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 400
951 | Super intendence | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 401
952 | Super intendence | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 402
953 | Super intendence | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 403
954 | Super intendence | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 404
955 | Super intendence | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 405
956 | Super intendence | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 406
957 | Super intendence | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 407
958 | Super intendence | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 408
959 | Super intendence | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 409
960 | Super intendence | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 410
961 | Super intendence | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 411
962 | Super intendence | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
963 | Super intendence | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
964 | Super intendence | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
965 | Super intendence | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13079
966 | Super intendence | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13080
967 | Super intendence | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5418
968 | Super intendence | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5419
969 | Super intendence | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5420
970 | Super intendence | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5421
971 | Super intendence | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5422
972 | Super intendence | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5423
973 | Super intendence | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5424
974 | Super intendence | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5425
975 | Super intendence | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5426
976 | Super intendence | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5427
977 | Super intendence | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5428
978 | Super intendence | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5429
979 | Super intendence | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5430
980 | Super intendence | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5431
981 | Super intendence | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5432
982 | Super intendence | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5433
983 | Super intendence | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5434
984 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5435
985 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5436
986 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5437
987 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5438
988 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5439
989 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5440
990 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5441