## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Substation Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Substation Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Substation Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Substation Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Substation Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Substation Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Agarpara CKT-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 16
29 | Agarpara CKT-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 17
30 | Agarpara CKT-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 18
31 | Agarpara CKT-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 19
32 | Agarpara CKT-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 20
33 | Agarpara CKT-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 21
34 | Agarpara CKT-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 22
35 | Agarpara CKT-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 23
36 | Agarpara CKT-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 24
37 | Agarpara CKT-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 25
38 | Agarpara CKT-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 26
39 | Agarpara CKT-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 27
40 | Agarpara CKT-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13000
41 | Agarpara CKT-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13001
42 | Agarpara CKT-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13002
43 | Agarpara CKT-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10001
44 | Agarpara CKT-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10001
45 | Agarpara CKT-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5008
46 | Agarpara CKT-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5009
47 | Agarpara CKT-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5010
48 | Agarpara CKT-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5011
49 | Agarpara CKT-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5012
50 | Agarpara CKT-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5013
51 | Agarpara CKT-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5014
52 | Agarpara CKT-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5015
53 | Agarpara CKT-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5016
54 | Agarpara CKT-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5017
55 | Agarpara CKT-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5018
56 | Agarpara CKT-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5019
57 | Agarpara CKT-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5020
58 | Agarpara CKT-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5021
59 | Agarpara CKT-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5022
60 | Agarpara CKT-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
61 | Agarpara CKT-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
62 | Agarpara CKT-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5025
63 | Agarpara CKT-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5026
64 | Old Calcutta Ckt-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 28
65 | Old Calcutta Ckt-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 29
66 | Old Calcutta Ckt-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 30
67 | Old Calcutta Ckt-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 31
68 | Old Calcutta Ckt-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 32
69 | Old Calcutta Ckt-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 33
70 | Old Calcutta Ckt-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 34
71 | Old Calcutta Ckt-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 35
72 | Old Calcutta Ckt-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 36
73 | Old Calcutta Ckt-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 37
74 | Old Calcutta Ckt-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 38
75 | Old Calcutta Ckt-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 39
76 | Old Calcutta Ckt-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13003
77 | Old Calcutta Ckt-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13004
78 | Old Calcutta Ckt-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13005
79 | Old Calcutta Ckt-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10002
80 | Old Calcutta Ckt-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10002
81 | Old Calcutta Ckt-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5027
82 | Old Calcutta Ckt-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5028
83 | Old Calcutta Ckt-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5029
84 | Old Calcutta Ckt-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5030
85 | Old Calcutta Ckt-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5031
86 | Old Calcutta Ckt-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5032
87 | Old Calcutta Ckt-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5033
88 | Old Calcutta Ckt-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5034
89 | Old Calcutta Ckt-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5035
90 | Old Calcutta Ckt-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5036
91 | Old Calcutta Ckt-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5037
92 | Old Calcutta Ckt-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5038
93 | Old Calcutta Ckt-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5039
94 | Old Calcutta Ckt-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5040
95 | Old Calcutta Ckt-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5041
96 | Old Calcutta Ckt-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5042
97 | Old Calcutta Ckt-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5043
98 | Old Calcutta Ckt-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5044
99 | Old Calcutta Ckt-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5045
100 | Future Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 40
101 | Future Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 41
102 | Future Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 42
103 | Future Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 43
104 | Future Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 44
105 | Future Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 45
106 | Future Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 46
107 | Future Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 47
108 | Future Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 48
109 | Future Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 49
110 | Future Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 50
111 | Future Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 51
112 | Future Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 52
113 | Future Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 53
114 | Future Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 54
115 | Future Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 55
116 | Future Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 56
117 | Future Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 57
118 | Future Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 58
119 | Future Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 59
120 | Future Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 60
121 | Future Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 61
122 | Future Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 62
123 | Future Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 63
124 | Future Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
125 | Future Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
126 | Future Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
127 | Future Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
128 | Future Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
129 | Future Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
130 | Future Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5046
131 | Future Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5047
132 | Future Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5048
133 | Future Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5049
134 | Future Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5050
135 | Future Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5051
136 | Future Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5052
137 | Future Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5053
138 | Future Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5054
139 | Future Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5055
140 | Future Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5056
141 | Future Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5057
142 | Future Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5058
143 | Future Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5059
144 | Future Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5060
145 | Future Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5061
146 | Future Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5062
147 | Future Transformer-1(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 64
148 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 65
149 | Future Transformer-1(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 66 |  |  |  | AC CMR to be used
150 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 67
151 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 68
152 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 69
153 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 70
154 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 71
155 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
156 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
157 | Future Transformer-1(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5063
158 | Future Transformer-1(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5064
159 | Future Transformer-1(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5065
160 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 72
161 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 73
162 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 74
163 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 75
164 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 76
165 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 77
166 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 78
167 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 79
168 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 80
169 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 81
170 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 82
171 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 83
172 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 84
173 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 85
174 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 86
175 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 87
176 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 88
177 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 89
178 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 90
179 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 91
180 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 92
181 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 93
182 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 94
183 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 95
184 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
185 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
186 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
187 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
188 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
189 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
190 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5066
191 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5067
192 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5068
193 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5069
194 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5070
195 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5071
196 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5072
197 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5073
198 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5074
199 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5075
200 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5076
201 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5077
202 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5078
203 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5079
204 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5080
205 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5081
206 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5082
207 | Transformer-2(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 96
208 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 97
209 | Transformer-2(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 98 |  |  |  | AC CMR to be used
210 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 99
211 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 100
212 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 101
213 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 102
214 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 103
215 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
216 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
217 | Transformer-2(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5083
218 | Transformer-2(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5084
219 | Transformer-2(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5085
220 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 104
221 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 105
222 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 106
223 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 107
224 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 108
225 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 109
226 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 110
227 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 111
228 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 112
229 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 113
230 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 114
231 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 115
232 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 116
233 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 117
234 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 118
235 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 119
236 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 120
237 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 121
238 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 122
239 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 123
240 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 124
241 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 125
242 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 126
243 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 127
244 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
245 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
246 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
247 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
248 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10005
249 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10005
250 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5086
251 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5087
252 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5088
253 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5089
254 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5090
255 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5091
256 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5092
257 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5093
258 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5094
259 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5095
260 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5096
261 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5097
262 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5098
263 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5099
264 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5100
265 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5101
266 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5102
267 | Transformer-3(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 128
268 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 129
269 | Transformer-3(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 130 |  |  |  | AC CMR to be used
270 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 131
271 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 132
272 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 133
273 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 134
274 | Transformer-3(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 135
275 | Transformer-3(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
276 | Transformer-3(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
277 | Transformer-3(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5103
278 | Transformer-3(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5104
279 | Transformer-3(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5105
280 | Agarpara Ckt-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 136
281 | Agarpara Ckt-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 137
282 | Agarpara Ckt-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 138
283 | Agarpara Ckt-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 139
284 | Agarpara Ckt-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 140
285 | Agarpara Ckt-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 141
286 | Agarpara Ckt-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 142
287 | Agarpara Ckt-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 143
288 | Agarpara Ckt-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 144
289 | Agarpara Ckt-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 145
290 | Agarpara Ckt-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 146
291 | Agarpara Ckt-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 147
292 | Agarpara Ckt-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
293 | Agarpara Ckt-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
294 | Agarpara Ckt-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
295 | Agarpara Ckt-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
296 | Agarpara Ckt-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
297 | Agarpara Ckt-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5106
298 | Agarpara Ckt-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5107
299 | Agarpara Ckt-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5108
300 | Agarpara Ckt-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5109
301 | Agarpara Ckt-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5110
302 | Agarpara Ckt-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5111
303 | Agarpara Ckt-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5112
304 | Agarpara Ckt-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5113
305 | Agarpara Ckt-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5114
306 | Agarpara Ckt-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5115
307 | Agarpara Ckt-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5116
308 | Agarpara Ckt-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5117
309 | Agarpara Ckt-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5118
310 | Agarpara Ckt-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5119
311 | Agarpara Ckt-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5120
312 | Agarpara Ckt-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5121
313 | Agarpara Ckt-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5122
314 | Agarpara Ckt-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5123
315 | Agarpara Ckt-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5124
316 | Mohispota KMDA | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 148
317 | Mohispota KMDA | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 149
318 | Mohispota KMDA | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 150
319 | Mohispota KMDA | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 151
320 | Mohispota KMDA | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 152
321 | Mohispota KMDA | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 153
322 | Mohispota KMDA | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 154
323 | Mohispota KMDA | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 155
324 | Mohispota KMDA | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 156
325 | Mohispota KMDA | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 157
326 | Mohispota KMDA | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 158
327 | Mohispota KMDA | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 159
328 | Mohispota KMDA | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
329 | Mohispota KMDA | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
330 | Mohispota KMDA | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13029
331 | Mohispota KMDA | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
332 | Mohispota KMDA | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
333 | Mohispota KMDA | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5125
334 | Mohispota KMDA | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5126
335 | Mohispota KMDA | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5127
336 | Mohispota KMDA | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5128
337 | Mohispota KMDA | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5129
338 | Mohispota KMDA | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5130
339 | Mohispota KMDA | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5131
340 | Mohispota KMDA | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5132
341 | Mohispota KMDA | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5133
342 | Mohispota KMDA | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5134
343 | Mohispota KMDA | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5135
344 | Mohispota KMDA | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5136
345 | Mohispota KMDA | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5137
346 | Mohispota KMDA | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5138
347 | Mohispota KMDA | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5139
348 | Mohispota KMDA | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5140
349 | Mohispota KMDA | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5141
350 | Mohispota KMDA | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5142
351 | Mohispota KMDA | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5143
352 | Future New Incomer | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 160
353 | Future New Incomer | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 161
354 | Future New Incomer | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 162
355 | Future New Incomer | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 163
356 | Future New Incomer | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 164
357 | Future New Incomer | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 165
358 | Future New Incomer | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 166
359 | Future New Incomer | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 167
360 | Future New Incomer | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 168
361 | Future New Incomer | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 169
362 | Future New Incomer | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 170
363 | Future New Incomer | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 171
364 | Future New Incomer | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 172
365 | Future New Incomer | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
366 | Future New Incomer | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
367 | Future New Incomer | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
368 | Future New Incomer | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13031
369 | Future New Incomer | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13032
370 | Future New Incomer | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5144
371 | Future New Incomer | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5145
372 | Future New Incomer | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5146
373 | Future New Incomer | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5147
374 | Future New Incomer | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5148
375 | Future New Incomer | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5149
376 | Future New Incomer | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5150
377 | Future New Incomer | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5151
378 | Future New Incomer | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5152
379 | Future New Incomer | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5153
380 | Future New Incomer | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5154
381 | Future New Incomer | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5155
382 | Future New Incomer | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5156
383 | Future New Incomer | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5157
384 | Future New Incomer | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5158
385 | Future New Incomer | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5159
386 | Future New Incomer | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5160
387 | Future New Outgoing | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 173
388 | Future New Outgoing | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 174
389 | Future New Outgoing | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 175
390 | Future New Outgoing | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 176
391 | Future New Outgoing | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 177
392 | Future New Outgoing | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 178
393 | Future New Outgoing | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 179
394 | Future New Outgoing | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 180
395 | Future New Outgoing | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 181
396 | Future New Outgoing | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 182
397 | Future New Outgoing | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 183
398 | Future New Outgoing | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 184
399 | Future New Outgoing | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 185
400 | Future New Outgoing | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 186
401 | Future New Outgoing | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
402 | Future New Outgoing | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
403 | Future New Outgoing | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
404 | Future New Outgoing | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
405 | Future New Outgoing | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13035
406 | Future New Outgoing | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5161
407 | Future New Outgoing | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5162
408 | Future New Outgoing | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5163
409 | Future New Outgoing | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5164
410 | Future New Outgoing | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5165
411 | Future New Outgoing | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5166
412 | Future New Outgoing | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5167
413 | Future New Outgoing | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5168
414 | Future New Outgoing | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5169
415 | Future New Outgoing | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5170
416 | Future New Outgoing | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5171
417 | Future New Outgoing | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5172
418 | Future New Outgoing | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5173
419 | Future New Outgoing | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5174
420 | Future New Outgoing | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5175
421 | Future New Outgoing | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5176
422 | Future New Outgoing | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5177
423 | Stadium | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 187
424 | Stadium | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 188
425 | Stadium | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 189
426 | Stadium | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 190
427 | Stadium | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 191
428 | Stadium | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 192
429 | Stadium | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 193
430 | Stadium | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 194
431 | Stadium | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 195
432 | Stadium | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 196
433 | Stadium | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 197
434 | Stadium | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 198
435 | Stadium | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 199
436 | Stadium | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 200
437 | Stadium | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
438 | Stadium | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
439 | Stadium | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
440 | Stadium | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
441 | Stadium | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
442 | Stadium | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5178
443 | Stadium | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5179
444 | Stadium | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5180
445 | Stadium | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5181
446 | Stadium | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5182
447 | Stadium | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5183
448 | Stadium | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5184
449 | Stadium | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5185
450 | Stadium | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5186
451 | Stadium | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5187
452 | Stadium | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5188
453 | Stadium | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5189
454 | Stadium | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5190
455 | Stadium | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5191
456 | Stadium | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5192
457 | Stadium | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5193
458 | Stadium | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5194
459 | Kalyan Nagar | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 201
460 | Kalyan Nagar | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 202
461 | Kalyan Nagar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 203
462 | Kalyan Nagar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 204
463 | Kalyan Nagar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 205
464 | Kalyan Nagar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 206
465 | Kalyan Nagar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 207
466 | Kalyan Nagar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 208
467 | Kalyan Nagar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 209
468 | Kalyan Nagar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 210
469 | Kalyan Nagar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 211
470 | Kalyan Nagar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 212
471 | Kalyan Nagar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 213
472 | Kalyan Nagar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 214
473 | Kalyan Nagar | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
474 | Kalyan Nagar | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
475 | Kalyan Nagar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
476 | Kalyan Nagar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
477 | Kalyan Nagar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
478 | Kalyan Nagar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5195
479 | Kalyan Nagar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5196
480 | Kalyan Nagar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5197
481 | Kalyan Nagar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5198
482 | Kalyan Nagar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5199
483 | Kalyan Nagar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5200
484 | Kalyan Nagar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5201
485 | Kalyan Nagar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5202
486 | Kalyan Nagar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5203
487 | Kalyan Nagar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5204
488 | Kalyan Nagar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5205
489 | Kalyan Nagar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5206
490 | Kalyan Nagar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5207
491 | Kalyan Nagar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5208
492 | Kalyan Nagar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5209
493 | Kalyan Nagar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5210
494 | Kalyan Nagar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5211
495 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 215
496 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 216
497 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 217
498 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 218
499 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 219
500 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 220
501 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 221
502 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 222
503 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 223
504 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 224
505 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 225
506 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 226
507 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 227
508 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
509 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
510 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
511 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13043
512 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13044
513 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5212
514 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5213
515 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5214
516 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5215
517 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5216
518 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5217
519 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5218
520 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5219
521 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5220
522 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5221
523 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5222
524 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5223
525 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5224
526 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5225
527 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5226
528 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5227
529 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5228
530 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 228
531 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 229
532 | Bus Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 230
533 | Bus Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 231
534 | Bus Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 232
535 | Bus Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 233
536 | Bus Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 234
537 | Bus Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 235 |  |  |  | AC CMR to be used
538 | Bus Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 236
539 | Bus Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 237
540 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10013
541 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10013
542 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 238
543 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 239
544 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 240
545 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 241
546 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 242
547 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 243
548 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 244
549 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 245
550 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 246
551 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 247
552 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 248
553 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 249
554 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 250
555 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
556 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
557 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
558 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13046
559 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13047
560 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5229
561 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5230
562 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5231
563 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5232
564 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5233
565 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5234
566 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5235
567 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5236
568 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5237
569 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5238
570 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5239
571 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5240
572 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5241
573 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5242
574 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5243
575 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5244
576 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5245
577 | Rashmoni | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 251
578 | Rashmoni | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 252
579 | Rashmoni | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 253
580 | Rashmoni | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 254
581 | Rashmoni | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 255
582 | Rashmoni | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 256
583 | Rashmoni | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 257
584 | Rashmoni | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 258
585 | Rashmoni | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 259
586 | Rashmoni | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 260
587 | Rashmoni | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 261
588 | Rashmoni | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 262
589 | Rashmoni | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 263
590 | Rashmoni | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 264
591 | Rashmoni | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
592 | Rashmoni | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
593 | Rashmoni | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
594 | Rashmoni | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
595 | Rashmoni | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
596 | Rashmoni | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5246
597 | Rashmoni | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5247
598 | Rashmoni | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5248
599 | Rashmoni | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5249
600 | Rashmoni | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5250
601 | Rashmoni | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5251
602 | Rashmoni | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5252
603 | Rashmoni | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5253
604 | Rashmoni | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5254
605 | Rashmoni | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5255
606 | Rashmoni | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5256
607 | Rashmoni | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5257
608 | Rashmoni | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5258
609 | Rashmoni | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5259
610 | Rashmoni | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5260
611 | Rashmoni | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5261
612 | Rashmoni | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5262
613 | Sadhur More | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 265
614 | Sadhur More | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 266
615 | Sadhur More | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 267
616 | Sadhur More | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 268
617 | Sadhur More | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 269
618 | Sadhur More | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 270
619 | Sadhur More | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 271
620 | Sadhur More | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 272
621 | Sadhur More | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 273
622 | Sadhur More | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 274
623 | Sadhur More | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 275
624 | Sadhur More | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 276
625 | Sadhur More | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 277
626 | Sadhur More | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 278
627 | Sadhur More | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
628 | Sadhur More | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
629 | Sadhur More | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
630 | Sadhur More | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
631 | Sadhur More | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
632 | Sadhur More | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5263
633 | Sadhur More | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5264
634 | Sadhur More | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5265
635 | Sadhur More | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5266
636 | Sadhur More | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5267
637 | Sadhur More | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5268
638 | Sadhur More | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5269
639 | Sadhur More | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5270
640 | Sadhur More | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5271
641 | Sadhur More | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5272
642 | Sadhur More | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5273
643 | Sadhur More | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5274
644 | Sadhur More | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5275
645 | Sadhur More | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5276
646 | Sadhur More | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5277
647 | Sadhur More | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5278
648 | Sadhur More | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5279
649 | Dakshin Pally | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 279
650 | Dakshin Pally | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 280
651 | Dakshin Pally | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 281
652 | Dakshin Pally | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 282
653 | Dakshin Pally | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 283
654 | Dakshin Pally | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 284
655 | Dakshin Pally | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 285
656 | Dakshin Pally | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 286
657 | Dakshin Pally | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 287
658 | Dakshin Pally | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 288
659 | Dakshin Pally | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 289
660 | Dakshin Pally | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 290
661 | Dakshin Pally | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 291
662 | Dakshin Pally | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 292
663 | Dakshin Pally | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
664 | Dakshin Pally | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
665 | Dakshin Pally | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
666 | Dakshin Pally | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
667 | Dakshin Pally | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
668 | Dakshin Pally | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5280
669 | Dakshin Pally | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5281
670 | Dakshin Pally | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5282
671 | Dakshin Pally | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5283
672 | Dakshin Pally | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5284
673 | Dakshin Pally | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5285
674 | Dakshin Pally | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5286
675 | Dakshin Pally | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5287
676 | Dakshin Pally | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5288
677 | Dakshin Pally | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5289
678 | Dakshin Pally | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5290
679 | Dakshin Pally | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5291
680 | Dakshin Pally | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5292
681 | Dakshin Pally | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5293
682 | Dakshin Pally | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5294
683 | Dakshin Pally | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5295
684 | Dakshin Pally | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5296
685 | Super Feeder | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 293
686 | Super Feeder | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 294
687 | Super Feeder | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 295
688 | Super Feeder | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 296
689 | Super Feeder | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 297
690 | Super Feeder | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 298
691 | Super Feeder | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 299
692 | Super Feeder | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 300
693 | Super Feeder | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 301
694 | Super Feeder | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 302
695 | Super Feeder | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 303
696 | Super Feeder | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 304
697 | Super Feeder | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 305
698 | Super Feeder | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 306
699 | Super Feeder | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
700 | Super Feeder | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
701 | Super Feeder | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
702 | Super Feeder | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
703 | Super Feeder | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
704 | Super Feeder | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5297
705 | Super Feeder | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5298
706 | Super Feeder | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5299
707 | Super Feeder | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5300
708 | Super Feeder | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5301
709 | Super Feeder | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5302
710 | Super Feeder | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5303
711 | Super Feeder | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5304
712 | Super Feeder | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5305
713 | Super Feeder | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5306
714 | Super Feeder | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5307
715 | Super Feeder | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5308
716 | Super Feeder | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5309
717 | Super Feeder | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5310
718 | Super Feeder | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5311
719 | Super Feeder | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5312
720 | Super Feeder | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5313
721 | Keyamore | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 307
722 | Keyamore | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 308
723 | Keyamore | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 309
724 | Keyamore | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 310
725 | Keyamore | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 311
726 | Keyamore | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 312
727 | Keyamore | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 313
728 | Keyamore | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 314
729 | Keyamore | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 315
730 | Keyamore | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 316
731 | Keyamore | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 317
732 | Keyamore | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 318
733 | Keyamore | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 319
734 | Keyamore | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 320
735 | Keyamore | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
736 | Keyamore | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
737 | Keyamore | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
738 | Keyamore | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
739 | Keyamore | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
740 | Keyamore | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5314
741 | Keyamore | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5315
742 | Keyamore | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5316
743 | Keyamore | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5317
744 | Keyamore | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5318
745 | Keyamore | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5319
746 | Keyamore | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5320
747 | Keyamore | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5321
748 | Keyamore | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5322
749 | Keyamore | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5323
750 | Keyamore | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5324
751 | Keyamore | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5325
752 | Keyamore | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5326
753 | Keyamore | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5327
754 | Keyamore | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5328
755 | Keyamore | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5329
756 | Keyamore | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5330
757 | Future New Bus Coupler | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 321
758 | Future New Bus Coupler | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 322
759 | Future New Bus Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 323
760 | Future New Bus Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 324
761 | Future New Bus Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 325
762 | Future New Bus Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 326
763 | Future New Bus Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 327
764 | Future New Bus Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 328 |  |  |  | AC CMR to be used
765 | Future New Bus Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 329
766 | Future New Bus Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 330
767 | Future New Bus Coupler | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10020
768 | Future New Bus Coupler | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10020
769 | Future New Outgoing | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 331
770 | Future New Outgoing | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 332
771 | Future New Outgoing | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 333
772 | Future New Outgoing | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 334
773 | Future New Outgoing | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 335
774 | Future New Outgoing | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 336
775 | Future New Outgoing | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 337
776 | Future New Outgoing | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 338
777 | Future New Outgoing | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 339
778 | Future New Outgoing | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 340
779 | Future New Outgoing | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 341
780 | Future New Outgoing | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 342
781 | Future New Outgoing | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 343
782 | Future New Outgoing | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 344
783 | Future New Outgoing | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
784 | Future New Outgoing | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
785 | Future New Outgoing | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
786 | Future New Outgoing | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
787 | Future New Outgoing | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
788 | Future New Outgoing | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5331
789 | Future New Outgoing | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5332
790 | Future New Outgoing | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5333
791 | Future New Outgoing | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5334
792 | Future New Outgoing | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5335
793 | Future New Outgoing | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5336
794 | Future New Outgoing | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5337
795 | Future New Outgoing | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5338
796 | Future New Outgoing | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5339
797 | Future New Outgoing | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5340
798 | Future New Outgoing | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5341
799 | Future New Outgoing | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5342
800 | Future New Outgoing | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5343
801 | Future New Outgoing | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5344
802 | Future New Outgoing | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5345
803 | Future New Outgoing | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5346
804 | Future New Outgoing | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5347
805 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5348
806 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5349
807 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5350
808 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5351
809 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5352
810 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5353
811 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5354