## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Substation Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Substation Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Substation Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Substation Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Substation Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Substation Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5008
29 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5009
30 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5010
31 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5011
32 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5012
33 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5013
34 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5014
35 | Old Calcutta | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 16
36 | Old Calcutta | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 17
37 | Old Calcutta | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 18
38 | Old Calcutta | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 19
39 | Old Calcutta | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 20
40 | Old Calcutta | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 21
41 | Old Calcutta | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 22
42 | Old Calcutta | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 23
43 | Old Calcutta | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 24
44 | Old Calcutta | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 25
45 | Old Calcutta | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 26
46 | Old Calcutta | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 27
47 | Old Calcutta | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13000
48 | Old Calcutta | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13001
49 | Old Calcutta | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13002
50 | Old Calcutta | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10001
51 | Old Calcutta | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10001
52 | Old Calcutta | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5015
53 | Old Calcutta | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5016
54 | Old Calcutta | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5017
55 | Old Calcutta | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5018
56 | Old Calcutta | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5019
57 | Old Calcutta | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5020
58 | Old Calcutta | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5021
59 | Old Calcutta | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5022
60 | Old Calcutta | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5023
61 | Old Calcutta | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5024
62 | Old Calcutta | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5025
63 | Old Calcutta | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5026
64 | Old Calcutta | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5027
65 | Old Calcutta | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5028
66 | Old Calcutta | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5029
67 | Old Calcutta | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5030
68 | Old Calcutta | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5031
69 | Old Calcutta | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5032
70 | Old Calcutta | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5033
71 | Royalpark | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 28
72 | Royalpark | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 29
73 | Royalpark | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 30
74 | Royalpark | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 31
75 | Royalpark | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 32
76 | Royalpark | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 33
77 | Royalpark | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 34
78 | Royalpark | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 35
79 | Royalpark | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 36
80 | Royalpark | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 37
81 | Royalpark | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 38
82 | Royalpark | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 39
83 | Royalpark | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13003
84 | Royalpark | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13004
85 | Royalpark | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13005
86 | Royalpark | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10002
87 | Royalpark | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10002
88 | Royalpark | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5034
89 | Royalpark | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5035
90 | Royalpark | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5036
91 | Royalpark | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5037
92 | Royalpark | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5038
93 | Royalpark | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5039
94 | Royalpark | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5040
95 | Royalpark | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5041
96 | Royalpark | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5042
97 | Royalpark | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5043
98 | Royalpark | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5044
99 | Royalpark | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5045
100 | Royalpark | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5046
101 | Royalpark | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5047
102 | Royalpark | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5048
103 | Royalpark | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5049
104 | Royalpark | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5050
105 | Royalpark | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5051
106 | Royalpark | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5052
107 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 40
108 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 41
109 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 42
110 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 43
111 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 44
112 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 45
113 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 46
114 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 47
115 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 48
116 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 49
117 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 50
118 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 51
119 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 52
120 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 53
121 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 54
122 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 55
123 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 56
124 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 57
125 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 58
126 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 59
127 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 60
128 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 61
129 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 62
130 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 63
131 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
132 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
133 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
134 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
135 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
136 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
137 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5053
138 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5054
139 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5055
140 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5056
141 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5057
142 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5058
143 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5059
144 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5060
145 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5061
146 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5062
147 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5063
148 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5064
149 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5065
150 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5066
151 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5067
152 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5068
153 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5069
154 | Transformer-1(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 64
155 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 65
156 | Transformer-1(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 66 |  |  |  | AC CMR to be used
157 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 67
158 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 68
159 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 69
160 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 70
161 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 71
162 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
163 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
164 | Transformer-1(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5070
165 | Transformer-1(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5071
166 | Transformer-1(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5072
167 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 72
168 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 73
169 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 74
170 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 75
171 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 76
172 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 77
173 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 78
174 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 79
175 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 80
176 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 81
177 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 82
178 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 83
179 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 84
180 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 85
181 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 86
182 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 87
183 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 88
184 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 89
185 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 90
186 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 91
187 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 92
188 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 93
189 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 94
190 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 95
191 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
192 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
193 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
194 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
195 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
196 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
197 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5073
198 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5074
199 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5075
200 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5076
201 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5077
202 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5078
203 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5079
204 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5080
205 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5081
206 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5082
207 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5083
208 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5084
209 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5085
210 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5086
211 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5087
212 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5088
213 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5089
214 | Transformer-2(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 96
215 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 97
216 | Transformer-2(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 98 |  |  |  | AC CMR to be used
217 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 99
218 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 100
219 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 101
220 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 102
221 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 103
222 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
223 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
224 | Transformer-2(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5090
225 | Transformer-2(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5091
226 | Transformer-2(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5092
227 | Barrackpur Stadium | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 104
228 | Barrackpur Stadium | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 105
229 | Barrackpur Stadium | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 106
230 | Barrackpur Stadium | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 107
231 | Barrackpur Stadium | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 108
232 | Barrackpur Stadium | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 109
233 | Barrackpur Stadium | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 110
234 | Barrackpur Stadium | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 111
235 | Barrackpur Stadium | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 112
236 | Barrackpur Stadium | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 113
237 | Barrackpur Stadium | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 114
238 | Barrackpur Stadium | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 115
239 | Barrackpur Stadium | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 116
240 | Barrackpur Stadium | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 117
241 | Barrackpur Stadium | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
242 | Barrackpur Stadium | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
243 | Barrackpur Stadium | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
244 | Barrackpur Stadium | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13019
245 | Barrackpur Stadium | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13020
246 | Barrackpur Stadium | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5093
247 | Barrackpur Stadium | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5094
248 | Barrackpur Stadium | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5095
249 | Barrackpur Stadium | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5096
250 | Barrackpur Stadium | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5097
251 | Barrackpur Stadium | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5098
252 | Barrackpur Stadium | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5099
253 | Barrackpur Stadium | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5100
254 | Barrackpur Stadium | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5101
255 | Barrackpur Stadium | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5102
256 | Barrackpur Stadium | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5103
257 | Barrackpur Stadium | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5104
258 | Barrackpur Stadium | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5105
259 | Barrackpur Stadium | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5106
260 | Barrackpur Stadium | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5107
261 | Barrackpur Stadium | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5108
262 | Barrackpur Stadium | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5109
263 | Kanthalia | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 118
264 | Kanthalia | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 119
265 | Kanthalia | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 120
266 | Kanthalia | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 121
267 | Kanthalia | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 122
268 | Kanthalia | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 123
269 | Kanthalia | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 124
270 | Kanthalia | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 125
271 | Kanthalia | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 126
272 | Kanthalia | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 127
273 | Kanthalia | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 128
274 | Kanthalia | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 129
275 | Kanthalia | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 130
276 | Kanthalia | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 131
277 | Kanthalia | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
278 | Kanthalia | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
279 | Kanthalia | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
280 | Kanthalia | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13022
281 | Kanthalia | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13023
282 | Kanthalia | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5110
283 | Kanthalia | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5111
284 | Kanthalia | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5112
285 | Kanthalia | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5113
286 | Kanthalia | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5114
287 | Kanthalia | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5115
288 | Kanthalia | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5116
289 | Kanthalia | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5117
290 | Kanthalia | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5118
291 | Kanthalia | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5119
292 | Kanthalia | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5120
293 | Kanthalia | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5121
294 | Kanthalia | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5122
295 | Kanthalia | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5123
296 | Kanthalia | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5124
297 | Kanthalia | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5125
298 | Kanthalia | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5126
299 | Shilpanchal | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 132
300 | Shilpanchal | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 133
301 | Shilpanchal | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 134
302 | Shilpanchal | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 135
303 | Shilpanchal | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 136
304 | Shilpanchal | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 137
305 | Shilpanchal | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 138
306 | Shilpanchal | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 139
307 | Shilpanchal | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 140
308 | Shilpanchal | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 141
309 | Shilpanchal | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 142
310 | Shilpanchal | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 143
311 | Shilpanchal | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 144
312 | Shilpanchal | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 145
313 | Shilpanchal | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
314 | Shilpanchal | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
315 | Shilpanchal | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
316 | Shilpanchal | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13025
317 | Shilpanchal | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13026
318 | Shilpanchal | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5127
319 | Shilpanchal | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5128
320 | Shilpanchal | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5129
321 | Shilpanchal | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5130
322 | Shilpanchal | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5131
323 | Shilpanchal | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5132
324 | Shilpanchal | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5133
325 | Shilpanchal | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5134
326 | Shilpanchal | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5135
327 | Shilpanchal | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5136
328 | Shilpanchal | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5137
329 | Shilpanchal | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5138
330 | Shilpanchal | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5139
331 | Shilpanchal | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5140
332 | Shilpanchal | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5141
333 | Shilpanchal | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5142
334 | Shilpanchal | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5143
335 | Wirelesspara | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 146
336 | Wirelesspara | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 147
337 | Wirelesspara | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 148
338 | Wirelesspara | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 149
339 | Wirelesspara | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 150
340 | Wirelesspara | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 151
341 | Wirelesspara | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 152
342 | Wirelesspara | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 153
343 | Wirelesspara | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 154
344 | Wirelesspara | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 155
345 | Wirelesspara | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 156
346 | Wirelesspara | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 157
347 | Wirelesspara | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 158
348 | Wirelesspara | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 159
349 | Wirelesspara | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
350 | Wirelesspara | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
351 | Wirelesspara | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
352 | Wirelesspara | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13028
353 | Wirelesspara | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13029
354 | Wirelesspara | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5144
355 | Wirelesspara | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5145
356 | Wirelesspara | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5146
357 | Wirelesspara | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5147
358 | Wirelesspara | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5148
359 | Wirelesspara | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5149
360 | Wirelesspara | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5150
361 | Wirelesspara | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5151
362 | Wirelesspara | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5152
363 | Wirelesspara | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5153
364 | Wirelesspara | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5154
365 | Wirelesspara | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5155
366 | Wirelesspara | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5156
367 | Wirelesspara | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5157
368 | Wirelesspara | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5158
369 | Wirelesspara | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5159
370 | Wirelesspara | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5160
371 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 160
372 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 161
373 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 162
374 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 163
375 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 164
376 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 165
377 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 166
378 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 167
379 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 168
380 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 169
381 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 170
382 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 171
383 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 172
384 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
385 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
386 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
387 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13031
388 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13032
389 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5161
390 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5162
391 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5163
392 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5164
393 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5165
394 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5166
395 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5167
396 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5168
397 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5169
398 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5170
399 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5171
400 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5172
401 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5173
402 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5174
403 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5175
404 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5176
405 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5177
406 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 173
407 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 174
408 | Bus Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 175
409 | Bus Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 176
410 | Bus Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 177
411 | Bus Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 178
412 | Bus Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 179
413 | Bus Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 180 |  |  |  | AC CMR to be used
414 | Bus Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 181
415 | Bus Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 182
416 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10010
417 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10010
418 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 183
419 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 184
420 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 185
421 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 186
422 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 187
423 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 188
424 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 189
425 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 190
426 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 191
427 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 192
428 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 193
429 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 194
430 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 195
431 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
432 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
433 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
434 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13034
435 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13035
436 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5178
437 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5179
438 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5180
439 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5181
440 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5182
441 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5183
442 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5184
443 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5185
444 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5186
445 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5187
446 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5188
447 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5189
448 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5190
449 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5191
450 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5192
451 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5193
452 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5194
453 | Udayan Home | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 196
454 | Udayan Home | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 197
455 | Udayan Home | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 198
456 | Udayan Home | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 199
457 | Udayan Home | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 200
458 | Udayan Home | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 201
459 | Udayan Home | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 202
460 | Udayan Home | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 203
461 | Udayan Home | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 204
462 | Udayan Home | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 205
463 | Udayan Home | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 206
464 | Udayan Home | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 207
465 | Udayan Home | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 208
466 | Udayan Home | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 209
467 | Udayan Home | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
468 | Udayan Home | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
469 | Udayan Home | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
470 | Udayan Home | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
471 | Udayan Home | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
472 | Udayan Home | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5195
473 | Udayan Home | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5196
474 | Udayan Home | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5197
475 | Udayan Home | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5198
476 | Udayan Home | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5199
477 | Udayan Home | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5200
478 | Udayan Home | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5201
479 | Udayan Home | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5202
480 | Udayan Home | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5203
481 | Udayan Home | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5204
482 | Udayan Home | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5205
483 | Udayan Home | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5206
484 | Udayan Home | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5207
485 | Udayan Home | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5208
486 | Udayan Home | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5209
487 | Udayan Home | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5210
488 | Udayan Home | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5211
489 | Jffarpur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 210
490 | Jffarpur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 211
491 | Jffarpur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 212
492 | Jffarpur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 213
493 | Jffarpur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 214
494 | Jffarpur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 215
495 | Jffarpur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 216
496 | Jffarpur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 217
497 | Jffarpur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 218
498 | Jffarpur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 219
499 | Jffarpur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 220
500 | Jffarpur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 221
501 | Jffarpur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 222
502 | Jffarpur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 223
503 | Jffarpur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
504 | Jffarpur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
505 | Jffarpur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
506 | Jffarpur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
507 | Jffarpur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
508 | Jffarpur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5212
509 | Jffarpur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5213
510 | Jffarpur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5214
511 | Jffarpur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5215
512 | Jffarpur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5216
513 | Jffarpur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5217
514 | Jffarpur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5218
515 | Jffarpur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5219
516 | Jffarpur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5220
517 | Jffarpur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5221
518 | Jffarpur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5222
519 | Jffarpur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5223
520 | Jffarpur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5224
521 | Jffarpur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5225
522 | Jffarpur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5226
523 | Jffarpur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5227
524 | Jffarpur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5228
525 | Matharangi | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 224
526 | Matharangi | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 225
527 | Matharangi | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 226
528 | Matharangi | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 227
529 | Matharangi | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 228
530 | Matharangi | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 229
531 | Matharangi | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 230
532 | Matharangi | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 231
533 | Matharangi | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 232
534 | Matharangi | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 233
535 | Matharangi | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 234
536 | Matharangi | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 235
537 | Matharangi | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 236
538 | Matharangi | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 237
539 | Matharangi | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
540 | Matharangi | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
541 | Matharangi | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
542 | Matharangi | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
543 | Matharangi | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
544 | Matharangi | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5229
545 | Matharangi | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5230
546 | Matharangi | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5231
547 | Matharangi | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5232
548 | Matharangi | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5233
549 | Matharangi | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5234
550 | Matharangi | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5235
551 | Matharangi | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5236
552 | Matharangi | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5237
553 | Matharangi | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5238
554 | Matharangi | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5239
555 | Matharangi | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5240
556 | Matharangi | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5241
557 | Matharangi | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5242
558 | Matharangi | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5243
559 | Matharangi | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5244
560 | Matharangi | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5245
561 | Debpukur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 238
562 | Debpukur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 239
563 | Debpukur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 240
564 | Debpukur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 241
565 | Debpukur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 242
566 | Debpukur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 243
567 | Debpukur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 244
568 | Debpukur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 245
569 | Debpukur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 246
570 | Debpukur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 247
571 | Debpukur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 248
572 | Debpukur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 249
573 | Debpukur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 250
574 | Debpukur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 251
575 | Debpukur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
576 | Debpukur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
577 | Debpukur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
578 | Debpukur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
579 | Debpukur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
580 | Debpukur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5246
581 | Debpukur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5247
582 | Debpukur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5248
583 | Debpukur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5249
584 | Debpukur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5250
585 | Debpukur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5251
586 | Debpukur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5252
587 | Debpukur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5253
588 | Debpukur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5254
589 | Debpukur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5255
590 | Debpukur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5256
591 | Debpukur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5257
592 | Debpukur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5258
593 | Debpukur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5259
594 | Debpukur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5260
595 | Debpukur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5261
596 | Debpukur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5262
597 | Future Spare O/G-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 252
598 | Future Spare O/G-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 253
599 | Future Spare O/G-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 254
600 | Future Spare O/G-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 255
601 | Future Spare O/G-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 256
602 | Future Spare O/G-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 257
603 | Future Spare O/G-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 258
604 | Future Spare O/G-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 259
605 | Future Spare O/G-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 260
606 | Future Spare O/G-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 261
607 | Future Spare O/G-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 262
608 | Future Spare O/G-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 263
609 | Future Spare O/G-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 264
610 | Future Spare O/G-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 265
611 | Future Spare O/G-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
612 | Future Spare O/G-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
613 | Future Spare O/G-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
614 | Future Spare O/G-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
615 | Future Spare O/G-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
616 | Future Spare O/G-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5263
617 | Future Spare O/G-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5264
618 | Future Spare O/G-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5265
619 | Future Spare O/G-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5266
620 | Future Spare O/G-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5267
621 | Future Spare O/G-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5268
622 | Future Spare O/G-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5269
623 | Future Spare O/G-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5270
624 | Future Spare O/G-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5271
625 | Future Spare O/G-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5272
626 | Future Spare O/G-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5273
627 | Future Spare O/G-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5274
628 | Future Spare O/G-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5275
629 | Future Spare O/G-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5276
630 | Future Spare O/G-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5277
631 | Future Spare O/G-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5278
632 | Future Spare O/G-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5279
633 | Future Spare O/G-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 266
634 | Future Spare O/G-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 267
635 | Future Spare O/G-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 268
636 | Future Spare O/G-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 269
637 | Future Spare O/G-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 270
638 | Future Spare O/G-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 271
639 | Future Spare O/G-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 272
640 | Future Spare O/G-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 273
641 | Future Spare O/G-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 274
642 | Future Spare O/G-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 275
643 | Future Spare O/G-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 276
644 | Future Spare O/G-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 277
645 | Future Spare O/G-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 278
646 | Future Spare O/G-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 279
647 | Future Spare O/G-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
648 | Future Spare O/G-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
649 | Future Spare O/G-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
650 | Future Spare O/G-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
651 | Future Spare O/G-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
652 | Future Spare O/G-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5280
653 | Future Spare O/G-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5281
654 | Future Spare O/G-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5282
655 | Future Spare O/G-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5283
656 | Future Spare O/G-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5284
657 | Future Spare O/G-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5285
658 | Future Spare O/G-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5286
659 | Future Spare O/G-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5287
660 | Future Spare O/G-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5288
661 | Future Spare O/G-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5289
662 | Future Spare O/G-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5290
663 | Future Spare O/G-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5291
664 | Future Spare O/G-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5292
665 | Future Spare O/G-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5293
666 | Future Spare O/G-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5294
667 | Future Spare O/G-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5295
668 | Future Spare O/G-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5296