## Signal List
SCADA/Advanced Distribution Management System (ADMS)
SL.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | Ac Low Voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Substation Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Substation Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Substation Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Substation Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Substation Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Substation Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5008
29 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5009
30 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5010
31 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5011
32 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5012
33 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5013
34 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5014
35 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
36 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
37 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
38 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
39 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
40 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
41 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
42 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
43 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
44 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
45 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
46 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
47 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
48 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
49 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
50 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
51 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
52 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
53 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
54 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
55 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
56 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
57 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
58 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
59 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
60 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
61 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
62 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
63 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
64 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
65 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5A | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5025
76 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5026
77 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5027
78 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5028
79 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5029
80 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5030
81 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5031
82 | Transfomer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
83 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
84 | Transfomer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
85 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
86 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
87 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
88 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
89 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
90 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
91 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
92 | Transfomer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5032
93 | Transfomer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5033
94 | Transfomer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5034
95 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
96 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
97 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
98 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
99 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
100 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
101 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
102 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
103 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
104 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
105 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
106 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
107 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
108 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
109 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
110 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
111 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
112 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
113 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
114 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
115 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
116 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
117 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
118 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
119 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
120 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
121 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
122 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
123 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
124 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
125 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5A | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5045
136 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5046
137 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5047
138 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5048
139 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5049
140 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5050
141 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5051
142 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
144 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
146 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
147 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
148 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
149 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
150 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
151 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
152 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5052
153 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5053
154 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5054
155 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 80
156 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 81
157 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
158 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
159 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
160 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
161 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
162 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
163 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
164 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
165 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
166 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
167 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
168 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
169 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
170 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
171 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
172 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
173 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
174 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
175 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
176 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
177 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
178 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
179 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
180 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
181 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
182 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
183 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
184 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
185 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5A | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5065
196 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5066
197 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5067
198 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5068
199 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5069
200 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5070
201 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5071
202 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
204 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
206 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
207 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
208 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
209 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
210 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
211 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
212 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5072
213 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5073
214 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5074
215 | SPARE | 33kV | I/C + Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 112
216 | SPARE | 33kV | I/C + Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 113
217 | SPARE | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 114
218 | SPARE | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 115
219 | SPARE | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 116
220 | SPARE | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 117
221 | SPARE | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 118
222 | SPARE | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 119
223 | SPARE | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 120
224 | SPARE | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 121
225 | SPARE | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 122
226 | SPARE | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 123
227 | SPARE | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
228 | SPARE | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13019
229 | SPARE | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13020
230 | SPARE | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10004
231 | SPARE | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10004
232 | SPARE | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5075
233 | SPARE | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5076
234 | SPARE | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5077
235 | SPARE | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5078
236 | SPARE | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5079
237 | SPARE | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5080
238 | SPARE | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5081
239 | SPARE | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5082
240 | SPARE | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5083
241 | SPARE | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5084
242 | SPARE | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5085
243 | SPARE | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5086
244 | SPARE | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5087
245 | SPARE | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5088
246 | SPARE | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5089
247 | SPARE | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5090
248 | SPARE | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5091
249 | SPARE | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5092
250 | SPARE | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5093
251 | OUTGOING | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 124
252 | OUTGOING | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 125
253 | OUTGOING | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 126
254 | OUTGOING | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 127
255 | OUTGOING | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 128
256 | OUTGOING | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 129
257 | OUTGOING | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 130
258 | OUTGOING | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 131
259 | OUTGOING | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 132
260 | OUTGOING | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 133
261 | OUTGOING | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 134
262 | OUTGOING | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 135
263 | OUTGOING | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
264 | OUTGOING | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13022
265 | OUTGOING | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13023
266 | OUTGOING | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
267 | OUTGOING | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
268 | OUTGOING | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5094
269 | OUTGOING | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5095
270 | OUTGOING | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5096
271 | OUTGOING | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5097
272 | OUTGOING | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5098
273 | OUTGOING | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5099
274 | OUTGOING | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5100
275 | OUTGOING | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5101
276 | OUTGOING | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5102
277 | OUTGOING | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5103
278 | OUTGOING | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5104
279 | OUTGOING | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5105
280 | OUTGOING | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5106
281 | OUTGOING | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5107
282 | OUTGOING | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5108
283 | OUTGOING | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5109
284 | OUTGOING | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5110
285 | OUTGOING | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5111
286 | OUTGOING | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5112
287 | Silicon valley (CKT-1) | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 136
288 | Silicon valley (CKT-1) | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 137
289 | Silicon valley (CKT-1) | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 138
290 | Silicon valley (CKT-1) | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 139
291 | Silicon valley (CKT-1) | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 140
292 | Silicon valley (CKT-1) | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 141
293 | Silicon valley (CKT-1) | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 142
294 | Silicon valley (CKT-1) | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 143
295 | Silicon valley (CKT-1) | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 144
296 | Silicon valley (CKT-1) | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 145
297 | Silicon valley (CKT-1) | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 146
298 | Silicon valley (CKT-1) | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 147
299 | Silicon valley (CKT-1) | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
300 | Silicon valley (CKT-1) | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
301 | Silicon valley (CKT-1) | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
302 | Silicon valley (CKT-1) | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
303 | Silicon valley (CKT-1) | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
304 | Silicon valley (CKT-1) | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5113
305 | Silicon valley (CKT-1) | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5114
306 | Silicon valley (CKT-1) | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5115
307 | Silicon valley (CKT-1) | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5116
308 | Silicon valley (CKT-1) | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5117
309 | Silicon valley (CKT-1) | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5118
310 | Silicon valley (CKT-1) | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5119
311 | Silicon valley (CKT-1) | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5120
312 | Silicon valley (CKT-1) | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5121
313 | Silicon valley (CKT-1) | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5122
314 | Silicon valley (CKT-1) | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5123
315 | Silicon valley (CKT-1) | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5124
316 | Silicon valley (CKT-1) | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5125
317 | Silicon valley (CKT-1) | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5126
318 | Silicon valley (CKT-1) | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5127
319 | Silicon valley (CKT-1) | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5128
320 | Silicon valley (CKT-1) | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5129
321 | Silicon valley (CKT-1) | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5130
322 | Silicon valley (CKT-1) | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5131
323 | Silicon valley (CKT-2) | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 148
324 | Silicon valley (CKT-2) | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 149
325 | Silicon valley (CKT-2) | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 150
326 | Silicon valley (CKT-2) | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 151
327 | Silicon valley (CKT-2) | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 152
328 | Silicon valley (CKT-2) | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 153
329 | Silicon valley (CKT-2) | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 154
330 | Silicon valley (CKT-2) | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 155
331 | Silicon valley (CKT-2) | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 156
332 | Silicon valley (CKT-2) | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 157
333 | Silicon valley (CKT-2) | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 158
334 | Silicon valley (CKT-2) | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 159
335 | Silicon valley (CKT-2) | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
336 | Silicon valley (CKT-2) | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
337 | Silicon valley (CKT-2) | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13029
338 | Silicon valley (CKT-2) | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
339 | Silicon valley (CKT-2) | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
340 | Silicon valley (CKT-2) | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5132
341 | Silicon valley (CKT-2) | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5133
342 | Silicon valley (CKT-2) | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5134
343 | Silicon valley (CKT-2) | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5135
344 | Silicon valley (CKT-2) | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5136
345 | Silicon valley (CKT-2) | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5137
346 | Silicon valley (CKT-2) | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5138
347 | Silicon valley (CKT-2) | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5139
348 | Silicon valley (CKT-2) | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5140
349 | Silicon valley (CKT-2) | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5141
350 | Silicon valley (CKT-2) | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5142
351 | Silicon valley (CKT-2) | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5143
352 | Silicon valley (CKT-2) | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5144
353 | Silicon valley (CKT-2) | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5145
354 | Silicon valley (CKT-2) | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5146
355 | Silicon valley (CKT-2) | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5147
356 | Silicon valley (CKT-2) | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5148
357 | Silicon valley (CKT-2) | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5149
358 | Silicon valley (CKT-2) | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5150
359 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 160
360 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 161
361 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 162
362 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 163
363 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 164
364 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 165
365 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 166
366 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 167
367 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 168
368 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 169
369 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 170
370 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 171
371 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 172
372 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 173
373 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
374 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
375 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
376 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
377 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13032
378 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5151
379 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5152
380 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5153
381 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5154
382 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5155
383 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5156
384 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5157
385 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5158
386 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5159
387 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5160
388 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5161
389 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5162
390 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5163
391 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5164
392 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5165
393 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5166
394 | 2E-PHE(DPS)(OG-12) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5167
395 | OG-11 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 174
396 | OG-11 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 175
397 | OG-11 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 176
398 | OG-11 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 177
399 | OG-11 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 178
400 | OG-11 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 179
401 | OG-11 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 180
402 | OG-11 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 181
403 | OG-11 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 182
404 | OG-11 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 183
405 | OG-11 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 184
406 | OG-11 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 185
407 | OG-11 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 186
408 | OG-11 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 187
409 | OG-11 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
410 | OG-11 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
411 | OG-11 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
412 | OG-11 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
413 | OG-11 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13035
414 | OG-11 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5168
415 | OG-11 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5169
416 | OG-11 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5170
417 | OG-11 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5171
418 | OG-11 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5172
419 | OG-11 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5173
420 | OG-11 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5174
421 | OG-11 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5175
422 | OG-11 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5176
423 | OG-11 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5177
424 | OG-11 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5178
425 | OG-11 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5179
426 | OG-11 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5180
427 | OG-11 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5181
428 | OG-11 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5182
429 | OG-11 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5183
430 | OG-11 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5184
431 | Incomer-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 188
432 | Incomer-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 189
433 | Incomer-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 190
434 | Incomer-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 191
435 | Incomer-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 192
436 | Incomer-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 193
437 | Incomer-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 194
438 | Incomer-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 195
439 | Incomer-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 196
440 | Incomer-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 197
441 | Incomer-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 198
442 | Incomer-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 199
443 | Incomer-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 200
444 | Incomer-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
445 | Incomer-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
446 | Incomer-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
447 | Incomer-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
448 | Incomer-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13038
449 | Incomer-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5185
450 | Incomer-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5186
451 | Incomer-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5187
452 | Incomer-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5188
453 | Incomer-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5189
454 | Incomer-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5190
455 | Incomer-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5191
456 | Incomer-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5192
457 | Incomer-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5193
458 | Incomer-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5194
459 | Incomer-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5195
460 | Incomer-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5196
461 | Incomer-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5197
462 | Incomer-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5198
463 | Incomer-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5199
464 | Incomer-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5200
465 | Incomer-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5201
466 | OUTGOING-10 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 201
467 | OUTGOING-10 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 202
468 | OUTGOING-10 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 203
469 | OUTGOING-10 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 204
470 | OUTGOING-10 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 205
471 | OUTGOING-10 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 206
472 | OUTGOING-10 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 207
473 | OUTGOING-10 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 208
474 | OUTGOING-10 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 209
475 | OUTGOING-10 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 210
476 | OUTGOING-10 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 211
477 | OUTGOING-10 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 212
478 | OUTGOING-10 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 213
479 | OUTGOING-10 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 214
480 | OUTGOING-10 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
481 | OUTGOING-10 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
482 | OUTGOING-10 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
483 | OUTGOING-10 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
484 | OUTGOING-10 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
485 | OUTGOING-10 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5202
486 | OUTGOING-10 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5203
487 | OUTGOING-10 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5204
488 | OUTGOING-10 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5205
489 | OUTGOING-10 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5206
490 | OUTGOING-10 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5207
491 | OUTGOING-10 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5208
492 | OUTGOING-10 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5209
493 | OUTGOING-10 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5210
494 | OUTGOING-10 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5211
495 | OUTGOING-10 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5212
496 | OUTGOING-10 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5213
497 | OUTGOING-10 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5214
498 | OUTGOING-10 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5215
499 | OUTGOING-10 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5216
500 | OUTGOING-10 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5217
501 | OUTGOING-10 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5218
502 | OUTGOING-9 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 215
503 | OUTGOING-9 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 216
504 | OUTGOING-9 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 217
505 | OUTGOING-9 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 218
506 | OUTGOING-9 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 219
507 | OUTGOING-9 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 220
508 | OUTGOING-9 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 221
509 | OUTGOING-9 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 222
510 | OUTGOING-9 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 223
511 | OUTGOING-9 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 224
512 | OUTGOING-9 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 225
513 | OUTGOING-9 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 226
514 | OUTGOING-9 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 227
515 | OUTGOING-9 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 228
516 | OUTGOING-9 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
517 | OUTGOING-9 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
518 | OUTGOING-9 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
519 | OUTGOING-9 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
520 | OUTGOING-9 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
521 | OUTGOING-9 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5219
522 | OUTGOING-9 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5220
523 | OUTGOING-9 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5221
524 | OUTGOING-9 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5222
525 | OUTGOING-9 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5223
526 | OUTGOING-9 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5224
527 | OUTGOING-9 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5225
528 | OUTGOING-9 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5226
529 | OUTGOING-9 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5227
530 | OUTGOING-9 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5228
531 | OUTGOING-9 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5229
532 | OUTGOING-9 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5230
533 | OUTGOING-9 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5231
534 | OUTGOING-9 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5232
535 | OUTGOING-9 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5233
536 | OUTGOING-9 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5234
537 | OUTGOING-9 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5235
538 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 229
539 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 230
540 | BUSCOUPLER-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 231
541 | BUSCOUPLER-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 232
542 | BUSCOUPLER-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 233
543 | BUSCOUPLER-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 234
544 | BUSCOUPLER-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 235
545 | BUSCOUPLER-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 236 |  |  |  | AC CMR to be used
546 | BUSCOUPLER-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 237
547 | BUSCOUPLER-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 238
548 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10013
549 | BUSCOUPLER-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10013
550 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 239
551 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 240
552 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 241
553 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 242
554 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 243
555 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 244
556 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 245
557 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 246
558 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 247
559 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 248
560 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 249
561 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 250
562 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 251
563 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 252
564 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
565 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
566 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
567 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
568 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
569 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5236
570 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5237
571 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5238
572 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5239
573 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5240
574 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5241
575 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5242
576 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5243
577 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5244
578 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5245
579 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5246
580 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5247
581 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5248
582 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5249
583 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5250
584 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5251
585 | OUTGOING-8 (A.I.F.F) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5252
586 | OUTGOING-7 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 253
587 | OUTGOING-7 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 254
588 | OUTGOING-7 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 255
589 | OUTGOING-7 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 256
590 | OUTGOING-7 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 257
591 | OUTGOING-7 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 258
592 | OUTGOING-7 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 259
593 | OUTGOING-7 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 260
594 | OUTGOING-7 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 261
595 | OUTGOING-7 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 262
596 | OUTGOING-7 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 263
597 | OUTGOING-7 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 264
598 | OUTGOING-7 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 265
599 | OUTGOING-7 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 266
600 | OUTGOING-7 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
601 | OUTGOING-7 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
602 | OUTGOING-7 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
603 | OUTGOING-7 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
604 | OUTGOING-7 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
605 | OUTGOING-7 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5253
606 | OUTGOING-7 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5254
607 | OUTGOING-7 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5255
608 | OUTGOING-7 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5256
609 | OUTGOING-7 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5257
610 | OUTGOING-7 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5258
611 | OUTGOING-7 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5259
612 | OUTGOING-7 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5260
613 | OUTGOING-7 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5261
614 | OUTGOING-7 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5262
615 | OUTGOING-7 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5263
616 | OUTGOING-7 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5264
617 | OUTGOING-7 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5265
618 | OUTGOING-7 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5266
619 | OUTGOING-7 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5267
620 | OUTGOING-7 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5268
621 | OUTGOING-7 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5269
622 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 267
623 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 268
624 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 269
625 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 270
626 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 271
627 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 272
628 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 273
629 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 274
630 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 275
631 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 276
632 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 277
633 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 278
634 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 279
635 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
636 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
637 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
638 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13052
639 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13053
640 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5270
641 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5271
642 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5272
643 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5273
644 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5274
645 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5275
646 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5276
647 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5277
648 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5278
649 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5279
650 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5280
651 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5281
652 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5282
653 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5283
654 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5284
655 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5285
656 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5286
657 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 280
658 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 281
659 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 282
660 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 283
661 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 284
662 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 285
663 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 286
664 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 287
665 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 288
666 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 289
667 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 290
668 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 291
669 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 292
670 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 293
671 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
672 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
673 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
674 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
675 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
676 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5287
677 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5288
678 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5289
679 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5290
680 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5291
681 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5292
682 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5293
683 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5294
684 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5295
685 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5296
686 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5297
687 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5298
688 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5299
689 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5300
690 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5301
691 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5302
692 | OUTGOING-6 (2E-S/S INTERCONNECTOR) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5303
693 | OUTGOING-5 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 294
694 | OUTGOING-5 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 295
695 | OUTGOING-5 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 296
696 | OUTGOING-5 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 297
697 | OUTGOING-5 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 298
698 | OUTGOING-5 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 299
699 | OUTGOING-5 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 300
700 | OUTGOING-5 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 301
701 | OUTGOING-5 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 302
702 | OUTGOING-5 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 303
703 | OUTGOING-5 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 304
704 | OUTGOING-5 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 305
705 | OUTGOING-5 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 306
706 | OUTGOING-5 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 307
707 | OUTGOING-5 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
708 | OUTGOING-5 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
709 | OUTGOING-5 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
710 | OUTGOING-5 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
711 | OUTGOING-5 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
712 | OUTGOING-5 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5304
713 | OUTGOING-5 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5305
714 | OUTGOING-5 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5306
715 | OUTGOING-5 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5307
716 | OUTGOING-5 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5308
717 | OUTGOING-5 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5309
718 | OUTGOING-5 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5310
719 | OUTGOING-5 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5311
720 | OUTGOING-5 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5312
721 | OUTGOING-5 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5313
722 | OUTGOING-5 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5314
723 | OUTGOING-5 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5315
724 | OUTGOING-5 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5316
725 | OUTGOING-5 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5317
726 | OUTGOING-5 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5318
727 | OUTGOING-5 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5319
728 | OUTGOING-5 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5320
729 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 308
730 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 309
731 | BUSCOUPLER-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 310
732 | BUSCOUPLER-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 311
733 | BUSCOUPLER-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 312
734 | BUSCOUPLER-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 313
735 | BUSCOUPLER-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 314
736 | BUSCOUPLER-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 315 |  |  |  | AC CMR to be used
737 | BUSCOUPLER-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 316
738 | BUSCOUPLER-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 317
739 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10019
740 | BUSCOUPLER-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10019
741 | OUTGOING-4 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 318
742 | OUTGOING-4 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 319
743 | OUTGOING-4 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 320
744 | OUTGOING-4 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 321
745 | OUTGOING-4 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 322
746 | OUTGOING-4 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 323
747 | OUTGOING-4 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 324
748 | OUTGOING-4 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 325
749 | OUTGOING-4 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 326
750 | OUTGOING-4 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 327
751 | OUTGOING-4 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 328
752 | OUTGOING-4 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 329
753 | OUTGOING-4 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 330
754 | OUTGOING-4 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 331
755 | OUTGOING-4 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
756 | OUTGOING-4 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
757 | OUTGOING-4 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
758 | OUTGOING-4 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
759 | OUTGOING-4 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
760 | OUTGOING-4 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5321
761 | OUTGOING-4 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5322
762 | OUTGOING-4 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5323
763 | OUTGOING-4 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5324
764 | OUTGOING-4 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5325
765 | OUTGOING-4 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5326
766 | OUTGOING-4 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5327
767 | OUTGOING-4 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5328
768 | OUTGOING-4 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5329
769 | OUTGOING-4 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5330
770 | OUTGOING-4 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5331
771 | OUTGOING-4 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5332
772 | OUTGOING-4 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5333
773 | OUTGOING-4 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5334
774 | OUTGOING-4 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5335
775 | OUTGOING-4 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5336
776 | OUTGOING-4 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5337
777 | OUTGOING-3 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 332
778 | OUTGOING-3 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 333
779 | OUTGOING-3 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 334
780 | OUTGOING-3 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 335
781 | OUTGOING-3 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 336
782 | OUTGOING-3 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 337
783 | OUTGOING-3 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 338
784 | OUTGOING-3 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 339
785 | OUTGOING-3 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 340
786 | OUTGOING-3 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 341
787 | OUTGOING-3 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 342
788 | OUTGOING-3 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 343
789 | OUTGOING-3 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 344
790 | OUTGOING-3 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 345
791 | OUTGOING-3 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
792 | OUTGOING-3 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
793 | OUTGOING-3 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
794 | OUTGOING-3 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
795 | OUTGOING-3 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
796 | OUTGOING-3 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5338
797 | OUTGOING-3 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5339
798 | OUTGOING-3 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5340
799 | OUTGOING-3 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5341
800 | OUTGOING-3 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5342
801 | OUTGOING-3 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5343
802 | OUTGOING-3 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5344
803 | OUTGOING-3 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5345
804 | OUTGOING-3 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5346
805 | OUTGOING-3 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5347
806 | OUTGOING-3 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5348
807 | OUTGOING-3 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5349
808 | OUTGOING-3 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5350
809 | OUTGOING-3 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5351
810 | OUTGOING-3 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5352
811 | OUTGOING-3 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5353
812 | OUTGOING-3 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5354
813 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 346
814 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 347
815 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 348
816 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 349
817 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 350
818 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 351
819 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 352
820 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 353
821 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 354
822 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 355
823 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 356
824 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 357
825 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 358
826 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
827 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
828 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
829 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13067
830 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13068
831 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5355
832 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5356
833 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5357
834 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5358
835 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5359
836 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5360
837 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5361
838 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5362
839 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5363
840 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5364
841 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5365
842 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5366
843 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5367
844 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5368
845 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5369
846 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5370
847 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5371
848 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 359
849 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 360
850 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 361
851 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 362
852 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 363
853 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 364
854 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 365
855 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 366
856 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 367
857 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 368
858 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 369
859 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 370
860 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 371
861 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 372
862 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
863 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
864 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
865 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
866 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
867 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5372
868 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5373
869 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5374
870 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5375
871 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5376
872 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5377
873 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5378
874 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5379
875 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5380
876 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5381
877 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5382
878 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5383
879 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5384
880 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5385
881 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5386
882 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5387
883 | OUTGOING-2 (HIDGO Smart building | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5388
884 | OUTGOING-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 373
885 | OUTGOING-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 374
886 | OUTGOING-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 375
887 | OUTGOING-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 376
888 | OUTGOING-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 377
889 | OUTGOING-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 378
890 | OUTGOING-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 379
891 | OUTGOING-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 380
892 | OUTGOING-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 381
893 | OUTGOING-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 382
894 | OUTGOING-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 383
895 | OUTGOING-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 384
896 | OUTGOING-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 385
897 | OUTGOING-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 386
898 | OUTGOING-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
899 | OUTGOING-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
900 | OUTGOING-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
901 | OUTGOING-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
902 | OUTGOING-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
903 | OUTGOING-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5389
904 | OUTGOING-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5390
905 | OUTGOING-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5391
906 | OUTGOING-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5392
907 | OUTGOING-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5393
908 | OUTGOING-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5394
909 | OUTGOING-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5395
910 | OUTGOING-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5396
911 | OUTGOING-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5397
912 | OUTGOING-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5398
913 | OUTGOING-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5399
914 | OUTGOING-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5400
915 | OUTGOING-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5401
916 | OUTGOING-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5402
917 | OUTGOING-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5403
918 | OUTGOING-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5404
919 | OUTGOING-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5405