## Signal List
SCADA/Advanced Distribution Management System (ADMS)
SL.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | Sub-Station common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | Sub-Station common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Siddha pine | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 80
149 | Siddha pine | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 81
150 | Siddha pine | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 82
151 | Siddha pine | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 83
152 | Siddha pine | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 84
153 | Siddha pine | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 85
154 | Siddha pine | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 86
155 | Siddha pine | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 87
156 | Siddha pine | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 88
157 | Siddha pine | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 89
158 | Siddha pine | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 90
159 | Siddha pine | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 91
160 | Siddha pine | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 92
161 | Siddha pine | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 93
162 | Siddha pine | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10003
163 | Siddha pine | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10003
164 | Siddha pine | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13012
165 | Siddha pine | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13013
166 | Siddha pine | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13014
167 | Siddha pine | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5048
168 | Siddha pine | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5049
169 | Siddha pine | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5050
170 | Siddha pine | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5051
171 | Siddha pine | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5052
172 | Siddha pine | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5053
173 | Siddha pine | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5054
174 | Siddha pine | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5055
175 | Siddha pine | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5056
176 | Siddha pine | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5057
177 | Siddha pine | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5058
178 | Siddha pine | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5059
179 | Siddha pine | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5060
180 | Siddha pine | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5061
181 | Siddha pine | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5062
182 | Siddha pine | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5063
183 | Siddha pine | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5064
184 | Siddha Galaxy | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 94
185 | Siddha Galaxy | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 95
186 | Siddha Galaxy | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 96
187 | Siddha Galaxy | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 97
188 | Siddha Galaxy | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 98
189 | Siddha Galaxy | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 99
190 | Siddha Galaxy | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 100
191 | Siddha Galaxy | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 101
192 | Siddha Galaxy | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 102
193 | Siddha Galaxy | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 103
194 | Siddha Galaxy | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 104
195 | Siddha Galaxy | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 105
196 | Siddha Galaxy | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 106
197 | Siddha Galaxy | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 107
198 | Siddha Galaxy | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10004
199 | Siddha Galaxy | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10004
200 | Siddha Galaxy | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13015
201 | Siddha Galaxy | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13016
202 | Siddha Galaxy | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13017
203 | Siddha Galaxy | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5065
204 | Siddha Galaxy | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5066
205 | Siddha Galaxy | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5067
206 | Siddha Galaxy | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5068
207 | Siddha Galaxy | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5069
208 | Siddha Galaxy | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5070
209 | Siddha Galaxy | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5071
210 | Siddha Galaxy | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5072
211 | Siddha Galaxy | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5073
212 | Siddha Galaxy | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5074
213 | Siddha Galaxy | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5075
214 | Siddha Galaxy | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5076
215 | Siddha Galaxy | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5077
216 | Siddha Galaxy | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5078
217 | Siddha Galaxy | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5079
218 | Siddha Galaxy | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5080
219 | Siddha Galaxy | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5081
220 | Rajarhut1-Ring main | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 108
221 | Rajarhut1-Ring main | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 109
222 | Rajarhut1-Ring main | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 110
223 | Rajarhut1-Ring main | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 111
224 | Rajarhut1-Ring main | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 112
225 | Rajarhut1-Ring main | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 113
226 | Rajarhut1-Ring main | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 114
227 | Rajarhut1-Ring main | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 115
228 | Rajarhut1-Ring main | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 116
229 | Rajarhut1-Ring main | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 117
230 | Rajarhut1-Ring main | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 118
231 | Rajarhut1-Ring main | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 119
232 | Rajarhut1-Ring main | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 120
233 | Rajarhut1-Ring main | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 121
234 | Rajarhut1-Ring main | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
235 | Rajarhut1-Ring main | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
236 | Rajarhut1-Ring main | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13018
237 | Rajarhut1-Ring main | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13019
238 | Rajarhut1-Ring main | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13020
239 | Rajarhut1-Ring main | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5082
240 | Rajarhut1-Ring main | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5083
241 | Rajarhut1-Ring main | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5084
242 | Rajarhut1-Ring main | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5085
243 | Rajarhut1-Ring main | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5086
244 | Rajarhut1-Ring main | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5087
245 | Rajarhut1-Ring main | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5088
246 | Rajarhut1-Ring main | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5089
247 | Rajarhut1-Ring main | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5090
248 | Rajarhut1-Ring main | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5091
249 | Rajarhut1-Ring main | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5092
250 | Rajarhut1-Ring main | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5093
251 | Rajarhut1-Ring main | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5094
252 | Rajarhut1-Ring main | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5095
253 | Rajarhut1-Ring main | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5096
254 | Rajarhut1-Ring main | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5097
255 | Rajarhut1-Ring main | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5098
256 | Sidha gopalpur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 122
257 | Sidha gopalpur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 123
258 | Sidha gopalpur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 124
259 | Sidha gopalpur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 125
260 | Sidha gopalpur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 126
261 | Sidha gopalpur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 127
262 | Sidha gopalpur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 128
263 | Sidha gopalpur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 129
264 | Sidha gopalpur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 130
265 | Sidha gopalpur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 131
266 | Sidha gopalpur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 132
267 | Sidha gopalpur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 133
268 | Sidha gopalpur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 134
269 | Sidha gopalpur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 135
270 | Sidha gopalpur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
271 | Sidha gopalpur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
272 | Sidha gopalpur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13021
273 | Sidha gopalpur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13022
274 | Sidha gopalpur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13023
275 | Sidha gopalpur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5099
276 | Sidha gopalpur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5100
277 | Sidha gopalpur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5101
278 | Sidha gopalpur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5102
279 | Sidha gopalpur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5103
280 | Sidha gopalpur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5104
281 | Sidha gopalpur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5105
282 | Sidha gopalpur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5106
283 | Sidha gopalpur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5107
284 | Sidha gopalpur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5108
285 | Sidha gopalpur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5109
286 | Sidha gopalpur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5110
287 | Sidha gopalpur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5111
288 | Sidha gopalpur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5112
289 | Sidha gopalpur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5113
290 | Sidha gopalpur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5114
291 | Sidha gopalpur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5115
292 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 136
293 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 137
294 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 138
295 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 139
296 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 140
297 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 141
298 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 142
299 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 143
300 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 144
301 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 145
302 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 146
303 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 147
304 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 148
305 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
306 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
307 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
308 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
309 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13026
310 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5116
311 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5117
312 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5118
313 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5119
314 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5120
315 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5121
316 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5122
317 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5123
318 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5124
319 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5125
320 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5126
321 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5127
322 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5128
323 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5129
324 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5130
325 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5131
326 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5132
327 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 149
328 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 150
329 | Bus Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 151
330 | Bus Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 152
331 | Bus Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 153
332 | Bus Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 154
333 | Bus Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 155
334 | Bus Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 156 |  |  |  | AC CMR to be used
335 | Bus Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 157
336 | Bus Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 158
337 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10008
338 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10008
339 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 159
340 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 160
341 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 161
342 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 162
343 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 163
344 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 164
345 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 165
346 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 166
347 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 167
348 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 168
349 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 169
350 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 170
351 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 171
352 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
353 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
354 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
355 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
356 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13029
357 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5133
358 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5134
359 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5135
360 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5136
361 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5137
362 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5138
363 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5139
364 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5140
365 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5141
366 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5142
367 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5143
368 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5144
369 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5145
370 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5146
371 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5147
372 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5148
373 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5149
374 | Rajarhat2-shekharpur | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 172
375 | Rajarhat2-shekharpur | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 173
376 | Rajarhat2-shekharpur | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 174
377 | Rajarhat2-shekharpur | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 175
378 | Rajarhat2-shekharpur | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 176
379 | Rajarhat2-shekharpur | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 177
380 | Rajarhat2-shekharpur | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 178
381 | Rajarhat2-shekharpur | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 179
382 | Rajarhat2-shekharpur | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 180
383 | Rajarhat2-shekharpur | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 181
384 | Rajarhat2-shekharpur | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 182
385 | Rajarhat2-shekharpur | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 183
386 | Rajarhat2-shekharpur | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 184
387 | Rajarhat2-shekharpur | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 185
388 | Rajarhat2-shekharpur | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
389 | Rajarhat2-shekharpur | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
390 | Rajarhat2-shekharpur | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
391 | Rajarhat2-shekharpur | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
392 | Rajarhat2-shekharpur | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13032
393 | Rajarhat2-shekharpur | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5150
394 | Rajarhat2-shekharpur | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5151
395 | Rajarhat2-shekharpur | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5152
396 | Rajarhat2-shekharpur | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5153
397 | Rajarhat2-shekharpur | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5154
398 | Rajarhat2-shekharpur | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5155
399 | Rajarhat2-shekharpur | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5156
400 | Rajarhat2-shekharpur | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5157
401 | Rajarhat2-shekharpur | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5158
402 | Rajarhat2-shekharpur | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5159
403 | Rajarhat2-shekharpur | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5160
404 | Rajarhat2-shekharpur | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5161
405 | Rajarhat2-shekharpur | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5162
406 | Rajarhat2-shekharpur | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5163
407 | Rajarhat2-shekharpur | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5164
408 | Rajarhat2-shekharpur | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5165
409 | Rajarhat2-shekharpur | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5166
410 | Siddha X Nad | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 186
411 | Siddha X Nad | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 187
412 | Siddha X Nad | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 188
413 | Siddha X Nad | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 189
414 | Siddha X Nad | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 190
415 | Siddha X Nad | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 191
416 | Siddha X Nad | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 192
417 | Siddha X Nad | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 193
418 | Siddha X Nad | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 194
419 | Siddha X Nad | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 195
420 | Siddha X Nad | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 196
421 | Siddha X Nad | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 197
422 | Siddha X Nad | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 198
423 | Siddha X Nad | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 199
424 | Siddha X Nad | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
425 | Siddha X Nad | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
426 | Siddha X Nad | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
427 | Siddha X Nad | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
428 | Siddha X Nad | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13035
429 | Siddha X Nad | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5167
430 | Siddha X Nad | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5168
431 | Siddha X Nad | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5169
432 | Siddha X Nad | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5170
433 | Siddha X Nad | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5171
434 | Siddha X Nad | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5172
435 | Siddha X Nad | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5173
436 | Siddha X Nad | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5174
437 | Siddha X Nad | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5175
438 | Siddha X Nad | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5176
439 | Siddha X Nad | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5177
440 | Siddha X Nad | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5178
441 | Siddha X Nad | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5179
442 | Siddha X Nad | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5180
443 | Siddha X Nad | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5181
444 | Siddha X Nad | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5182
445 | Siddha X Nad | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5183
446 | Siddha-gopalpur-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 200
447 | Siddha-gopalpur-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 201
448 | Siddha-gopalpur-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 202
449 | Siddha-gopalpur-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 203
450 | Siddha-gopalpur-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 204
451 | Siddha-gopalpur-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 205
452 | Siddha-gopalpur-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 206
453 | Siddha-gopalpur-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 207
454 | Siddha-gopalpur-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 208
455 | Siddha-gopalpur-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 209
456 | Siddha-gopalpur-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 210
457 | Siddha-gopalpur-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 211
458 | Siddha-gopalpur-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 212
459 | Siddha-gopalpur-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 213
460 | Siddha-gopalpur-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
461 | Siddha-gopalpur-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
462 | Siddha-gopalpur-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
463 | Siddha-gopalpur-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
464 | Siddha-gopalpur-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
465 | Siddha-gopalpur-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5184
466 | Siddha-gopalpur-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5185
467 | Siddha-gopalpur-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5186
468 | Siddha-gopalpur-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5187
469 | Siddha-gopalpur-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5188
470 | Siddha-gopalpur-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5189
471 | Siddha-gopalpur-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5190
472 | Siddha-gopalpur-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5191
473 | Siddha-gopalpur-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5192
474 | Siddha-gopalpur-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5193
475 | Siddha-gopalpur-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5194
476 | Siddha-gopalpur-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5195
477 | Siddha-gopalpur-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5196
478 | Siddha-gopalpur-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5197
479 | Siddha-gopalpur-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5198
480 | Siddha-gopalpur-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5199
481 | Siddha-gopalpur-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5200
482 | Siddha pine wood | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 214
483 | Siddha pine wood | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 215
484 | Siddha pine wood | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 216
485 | Siddha pine wood | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 217
486 | Siddha pine wood | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 218
487 | Siddha pine wood | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 219
488 | Siddha pine wood | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 220
489 | Siddha pine wood | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 221
490 | Siddha pine wood | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 222
491 | Siddha pine wood | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 223
492 | Siddha pine wood | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 224
493 | Siddha pine wood | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 225
494 | Siddha pine wood | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 226
495 | Siddha pine wood | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 227
496 | Siddha pine wood | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
497 | Siddha pine wood | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
498 | Siddha pine wood | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
499 | Siddha pine wood | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
500 | Siddha pine wood | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
501 | Siddha pine wood | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5201
502 | Siddha pine wood | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5202
503 | Siddha pine wood | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5203
504 | Siddha pine wood | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5204
505 | Siddha pine wood | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5205
506 | Siddha pine wood | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5206
507 | Siddha pine wood | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5207
508 | Siddha pine wood | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5208
509 | Siddha pine wood | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5209
510 | Siddha pine wood | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5210
511 | Siddha pine wood | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5211
512 | Siddha pine wood | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5212
513 | Siddha pine wood | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5213
514 | Siddha pine wood | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5214
515 | Siddha pine wood | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5215
516 | Siddha pine wood | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5216
517 | Siddha pine wood | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5217
518 | Ascon era | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 228
519 | Ascon era | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 229
520 | Ascon era | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 230
521 | Ascon era | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 231
522 | Ascon era | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 232
523 | Ascon era | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 233
524 | Ascon era | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 234
525 | Ascon era | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 235
526 | Ascon era | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 236
527 | Ascon era | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 237
528 | Ascon era | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 238
529 | Ascon era | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 239
530 | Ascon era | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 240
531 | Ascon era | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 241
532 | Ascon era | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
533 | Ascon era | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
534 | Ascon era | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
535 | Ascon era | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
536 | Ascon era | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
537 | Ascon era | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5218
538 | Ascon era | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5219
539 | Ascon era | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5220
540 | Ascon era | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5221
541 | Ascon era | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5222
542 | Ascon era | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5223
543 | Ascon era | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5224
544 | Ascon era | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5225
545 | Ascon era | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5226
546 | Ascon era | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5227
547 | Ascon era | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5228
548 | Ascon era | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5229
549 | Ascon era | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5230
550 | Ascon era | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5231
551 | Ascon era | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5232
552 | Ascon era | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5233
553 | Ascon era | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5234
554 | Future OG1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 242
555 | Future OG1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 243
556 | Future OG1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 244
557 | Future OG1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 245
558 | Future OG1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 246
559 | Future OG1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 247
560 | Future OG1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 248
561 | Future OG1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 249
562 | Future OG1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 250
563 | Future OG1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 251
564 | Future OG1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 252
565 | Future OG1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 253
566 | Future OG1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 254
567 | Future OG1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 255
568 | Future OG1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
569 | Future OG1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
570 | Future OG1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
571 | Future OG1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
572 | Future OG1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
573 | Future OG1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5235
574 | Future OG1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5236
575 | Future OG1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5237
576 | Future OG1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5238
577 | Future OG1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5239
578 | Future OG1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5240
579 | Future OG1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5241
580 | Future OG1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5242
581 | Future OG1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5243
582 | Future OG1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5244
583 | Future OG1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5245
584 | Future OG1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5246
585 | Future OG1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5247
586 | Future OG1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5248
587 | Future OG1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5249
588 | Future OG1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5250
589 | Future OG1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5251
590 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5252
591 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5253
592 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5254
593 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5255
594 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5256
595 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5257
596 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5258