## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 110V DC-2 | 110V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 110V DC-2 | 110V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 110V DC-2 | 110V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 110V DC-2 | 110V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 110V DC-2 | 110V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 110V DC-2 | 110V | DC DIST. BOARD | DC load Voltage | AI |  | 0-110V DC | Hard | Transducer | 5005
20 | 110V DC-2 | 110V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 110V DC-2 | 110V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | DUMMY CB | 3000
23 | Sub-Station common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | DUMMY CB | 10000
24 | Sub-Station common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Madhumitha | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 80
149 | Madhumitha | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 81
150 | Madhumitha | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 82
151 | Madhumitha | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 83
152 | Madhumitha | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 84
153 | Madhumitha | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 85
154 | Madhumitha | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 86
155 | Madhumitha | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 87
156 | Madhumitha | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 88
157 | Madhumitha | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 89
158 | Madhumitha | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 90
159 | Madhumitha | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 91
160 | Madhumitha | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13012
161 | Madhumitha | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13013
162 | Madhumitha | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13014
163 | Madhumitha | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10003
164 | Madhumitha | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10003
165 | Madhumitha | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5048
166 | Madhumitha | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5049
167 | Madhumitha | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5050
168 | Madhumitha | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5051
169 | Madhumitha | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5052
170 | Madhumitha | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5053
171 | Madhumitha | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5054
172 | Madhumitha | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5055
173 | Madhumitha | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5056
174 | Madhumitha | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5057
175 | Madhumitha | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5058
176 | Madhumitha | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5059
177 | Madhumitha | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5060
178 | Madhumitha | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5061
179 | Madhumitha | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5062
180 | Madhumitha | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
181 | Madhumitha | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
182 | Madhumitha | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5065
183 | Madhumitha | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5066
184 | New town | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 92
185 | New town | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 93
186 | New town | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 94
187 | New town | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 95
188 | New town | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 96
189 | New town | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 97
190 | New town | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 98
191 | New town | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 99
192 | New town | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 100
193 | New town | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 101
194 | New town | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 102
195 | New town | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 103
196 | New town | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13015
197 | New town | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13016
198 | New town | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13017
199 | New town | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10004
200 | New town | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10004
201 | New town | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5067
202 | New town | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5068
203 | New town | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5069
204 | New town | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5070
205 | New town | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5071
206 | New town | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5072
207 | New town | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5073
208 | New town | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5074
209 | New town | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5075
210 | New town | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5076
211 | New town | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5077
212 | New town | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5078
213 | New town | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5079
214 | New town | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5080
215 | New town | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5081
216 | New town | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5082
217 | New town | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5083
218 | New town | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5084
219 | New town | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5085
220 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch on | SPI |  |  | Soft | IED | 104 |  |  |  | Applicable only for GIS as a additional.
221 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch off | SPI |  |  | Soft | IED | 105 |  |  |  | Applicable only for GIS as a additional.
222 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch on | SPI |  |  | Soft | IED | 106 |  |  |  | Applicable only for GIS as a additional.
223 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch off | SPI |  |  | Soft | IED | 107 |  |  |  | Applicable only for GIS as a additional.
224 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Busbar chamber gas pressure low | SPI |  |  | Soft | IED | 108 |  |  |  | Applicable only for GIS as a additional.
225 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Circuit breaker chamber gas pressure low | SPI |  |  | Soft | IED | 109 |  |  |  | Applicable only for GIS as a additional.
226 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch on | SPC |  |  | Hard | HDR | 13018 |  |  |  | Applicable only for GIS as a additional.
227 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch off | SPC |  |  | Hard | HDR | 13019 |  |  |  | Applicable only for GIS as a additional.
228 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch on | SPC |  |  | Hard | HDR | 13020 |  |  |  | Applicable only for GIS as a additional.
229 | 33kV Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch off | SPC |  |  | Hard | HDR | 13021 |  |  |  | Applicable only for GIS as a additional.
230 | 33kV Bus Coupler | 33kV | 33KV BC | Earth Switch2 on | SPI |  |  | Soft | IED | 110 |  |  |  | Applicable only for GIS as a additional.
231 | 33kV Bus Coupler | 33kV | 33KV BC | Earth Switch2 off | SPI |  |  | Soft | IED | 111 |  |  |  | Applicable only for GIS as a additional.
232 | 33kV Bus Coupler | 33kV | 33KV BC | Earth Switch2 on | SPC |  |  | Hard | HDR | 13022 |  |  |  | Applicable only for GIS as a additional.
233 | 33kV Bus Coupler | 33kV | 33KV BC | Earth Switch2 off | SPC |  |  | Hard | HDR | 13023 |  |  |  | Applicable only for GIS as a additional.
234 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER DS ON | SPI |  |  | Hard | CMR | 112 |  |  |  | Applicable only for GIS as a additional.
235 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER DS OFF | SPI |  |  | Hard | CMR | 113 |  |  |  | Applicable only for GIS as a additional.
236 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER DS ON | SPC |  |  | Hard | HDR | 13024 |  |  |  | Applicable only for GIS as a additional.
237 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER DS OFF | SPC |  |  | Hard | HDR | 13025 |  |  |  | Applicable only for GIS as a additional.
238 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH ON | SPI |  |  | Hard | CMR | 114 |  |  |  | Applicable only for GIS as a additional.
239 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH OFF | SPI |  |  | Hard | CMR | 115 |  |  |  | Applicable only for GIS as a additional.
240 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH ON | SPC |  |  | Hard | HDR | 13026 |  |  |  | Applicable only for GIS as a additional.
241 | 33kV Bus riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH OFF | SPC |  |  | Hard | HDR | 13027 |  |  |  | Applicable only for GIS as a additional.
242 | Salt lake | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 116
243 | Salt lake | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 117
244 | Salt lake | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 118
245 | Salt lake | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 119
246 | Salt lake | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 120
247 | Salt lake | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 121
248 | Salt lake | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 122
249 | Salt lake | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 123
250 | Salt lake | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 124
251 | Salt lake | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 125
252 | Salt lake | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 126
253 | Salt lake | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 127
254 | Salt lake | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13028
255 | Salt lake | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13029
256 | Salt lake | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13030
257 | Salt lake | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
258 | Salt lake | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
259 | Salt lake | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5086
260 | Salt lake | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5087
261 | Salt lake | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5088
262 | Salt lake | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5089
263 | Salt lake | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5090
264 | Salt lake | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5091
265 | Salt lake | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5092
266 | Salt lake | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5093
267 | Salt lake | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5094
268 | Salt lake | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5095
269 | Salt lake | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5096
270 | Salt lake | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5097
271 | Salt lake | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5098
272 | Salt lake | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5099
273 | Salt lake | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5100
274 | Salt lake | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5101
275 | Salt lake | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5102
276 | Salt lake | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5103
277 | Salt lake | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5104
278 | Station Transformer | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5105
279 | Station Transformer | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5106
280 | Station Transformer | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5107
281 | Station Transformer | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5108
282 | Station Transformer | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5109
283 | Station Transformer | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5110
284 | Station Transformer | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5111
285 | Khash mahal | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 128
286 | Khash mahal | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 129
287 | Khash mahal | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 130
288 | Khash mahal | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 131
289 | Khash mahal | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 132
290 | Khash mahal | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 133
291 | Khash mahal | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 134
292 | Khash mahal | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 135
293 | Khash mahal | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 136
294 | Khash mahal | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 137
295 | Khash mahal | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 138
296 | Khash mahal | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 139
297 | Khash mahal | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 140
298 | Khash mahal | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 141
299 | Khash mahal | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
300 | Khash mahal | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
301 | Khash mahal | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13031
302 | Khash mahal | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13032
303 | Khash mahal | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13033
304 | Khash mahal | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5112
305 | Khash mahal | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5113
306 | Khash mahal | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5114
307 | Khash mahal | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5115
308 | Khash mahal | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5116
309 | Khash mahal | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5117
310 | Khash mahal | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5118
311 | Khash mahal | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5119
312 | Khash mahal | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5120
313 | Khash mahal | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5121
314 | Khash mahal | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5122
315 | Khash mahal | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5123
316 | Khash mahal | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5124
317 | Khash mahal | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5125
318 | Khash mahal | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5126
319 | Khash mahal | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5127
320 | Khash mahal | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5128
321 | Panache RMU-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 142
322 | Panache RMU-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 143
323 | Panache RMU-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 144
324 | Panache RMU-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 145
325 | Panache RMU-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 146
326 | Panache RMU-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 147
327 | Panache RMU-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 148
328 | Panache RMU-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 149
329 | Panache RMU-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 150
330 | Panache RMU-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 151
331 | Panache RMU-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 152
332 | Panache RMU-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 153
333 | Panache RMU-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 154
334 | Panache RMU-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 155
335 | Panache RMU-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
336 | Panache RMU-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
337 | Panache RMU-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13034
338 | Panache RMU-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13035
339 | Panache RMU-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13036
340 | Panache RMU-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5129
341 | Panache RMU-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5130
342 | Panache RMU-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5131
343 | Panache RMU-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5132
344 | Panache RMU-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5133
345 | Panache RMU-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5134
346 | Panache RMU-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5135
347 | Panache RMU-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5136
348 | Panache RMU-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5137
349 | Panache RMU-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5138
350 | Panache RMU-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5139
351 | Panache RMU-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5140
352 | Panache RMU-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5141
353 | Panache RMU-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5142
354 | Panache RMU-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5143
355 | Panache RMU-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5144
356 | Panache RMU-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5145
357 | Ideal RMU-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 156
358 | Ideal RMU-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 157
359 | Ideal RMU-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 158
360 | Ideal RMU-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 159
361 | Ideal RMU-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 160
362 | Ideal RMU-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 161
363 | Ideal RMU-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 162
364 | Ideal RMU-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 163
365 | Ideal RMU-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 164
366 | Ideal RMU-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 165
367 | Ideal RMU-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 166
368 | Ideal RMU-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 167
369 | Ideal RMU-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 168
370 | Ideal RMU-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 169
371 | Ideal RMU-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
372 | Ideal RMU-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
373 | Ideal RMU-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13037
374 | Ideal RMU-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13038
375 | Ideal RMU-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13039
376 | Ideal RMU-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5146
377 | Ideal RMU-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5147
378 | Ideal RMU-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5148
379 | Ideal RMU-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5149
380 | Ideal RMU-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5150
381 | Ideal RMU-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5151
382 | Ideal RMU-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5152
383 | Ideal RMU-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5153
384 | Ideal RMU-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5154
385 | Ideal RMU-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5155
386 | Ideal RMU-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5156
387 | Ideal RMU-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5157
388 | Ideal RMU-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5158
389 | Ideal RMU-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5159
390 | Ideal RMU-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5160
391 | Ideal RMU-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5161
392 | Ideal RMU-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5162
393 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 170
394 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 171
395 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 172
396 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 173
397 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 174
398 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 175
399 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 176
400 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 177
401 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 178
402 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 179
403 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 180
404 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 181
405 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 182
406 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
407 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
408 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13040
409 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13041
410 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13042
411 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5163
412 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5164
413 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5165
414 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5166
415 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5167
416 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5168
417 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5169
418 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5170
419 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5171
420 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5172
421 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5173
422 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5174
423 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5175
424 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5176
425 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5177
426 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5178
427 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5179
428 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 183
429 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 184
430 | Bus Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 185
431 | Bus Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 186
432 | Bus Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 187
433 | Bus Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 188
434 | Bus Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 189
435 | Bus Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 190 |  |  |  | AC CMR to be used
436 | Bus Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 191
437 | Bus Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 192
438 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10010
439 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10010
440 | Link road | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 193
441 | Link road | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 194
442 | Link road | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 195
443 | Link road | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 196
444 | Link road | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 197
445 | Link road | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 198
446 | Link road | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 199
447 | Link road | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 200
448 | Link road | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 201
449 | Link road | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 202
450 | Link road | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 203
451 | Link road | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 204
452 | Link road | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 205
453 | Link road | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 206
454 | Link road | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
455 | Link road | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
456 | Link road | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13043
457 | Link road | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13044
458 | Link road | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13045
459 | Link road | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5180
460 | Link road | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5181
461 | Link road | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5182
462 | Link road | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5183
463 | Link road | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5184
464 | Link road | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5185
465 | Link road | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5186
466 | Link road | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5187
467 | Link road | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5188
468 | Link road | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5189
469 | Link road | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5190
470 | Link road | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5191
471 | Link road | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5192
472 | Link road | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5193
473 | Link road | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5194
474 | Link road | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5195
475 | Link road | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5196
476 | Panache RMU-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 207
477 | Panache RMU-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 208
478 | Panache RMU-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 209
479 | Panache RMU-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 210
480 | Panache RMU-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 211
481 | Panache RMU-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 212
482 | Panache RMU-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 213
483 | Panache RMU-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 214
484 | Panache RMU-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 215
485 | Panache RMU-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 216
486 | Panache RMU-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 217
487 | Panache RMU-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 218
488 | Panache RMU-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 219
489 | Panache RMU-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 220
490 | Panache RMU-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
491 | Panache RMU-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
492 | Panache RMU-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13046
493 | Panache RMU-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13047
494 | Panache RMU-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13048
495 | Panache RMU-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5197
496 | Panache RMU-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5198
497 | Panache RMU-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5199
498 | Panache RMU-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5200
499 | Panache RMU-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5201
500 | Panache RMU-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5202
501 | Panache RMU-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5203
502 | Panache RMU-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5204
503 | Panache RMU-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5205
504 | Panache RMU-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5206
505 | Panache RMU-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5207
506 | Panache RMU-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5208
507 | Panache RMU-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5209
508 | Panache RMU-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5210
509 | Panache RMU-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5211
510 | Panache RMU-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5212
511 | Panache RMU-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5213
512 | Ideal RMU-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 221
513 | Ideal RMU-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 222
514 | Ideal RMU-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 223
515 | Ideal RMU-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 224
516 | Ideal RMU-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 225
517 | Ideal RMU-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 226
518 | Ideal RMU-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 227
519 | Ideal RMU-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 228
520 | Ideal RMU-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 229
521 | Ideal RMU-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 230
522 | Ideal RMU-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 231
523 | Ideal RMU-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 232
524 | Ideal RMU-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 233
525 | Ideal RMU-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 234
526 | Ideal RMU-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
527 | Ideal RMU-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
528 | Ideal RMU-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13049
529 | Ideal RMU-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13050
530 | Ideal RMU-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13051
531 | Ideal RMU-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5214
532 | Ideal RMU-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5215
533 | Ideal RMU-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5216
534 | Ideal RMU-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5217
535 | Ideal RMU-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5218
536 | Ideal RMU-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5219
537 | Ideal RMU-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5220
538 | Ideal RMU-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5221
539 | Ideal RMU-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5222
540 | Ideal RMU-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5223
541 | Ideal RMU-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5224
542 | Ideal RMU-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5225
543 | Ideal RMU-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5226
544 | Ideal RMU-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5227
545 | Ideal RMU-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5228
546 | Ideal RMU-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5229
547 | Ideal RMU-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5230
548 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 235
549 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 236
550 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 237
551 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 238
552 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 239
553 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 240
554 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 241
555 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 242
556 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 243
557 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 244
558 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 245
559 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 246
560 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 247
561 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
562 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
563 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13052
564 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13053
565 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13054
566 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5231
567 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5232
568 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5233
569 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5234
570 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5235
571 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5236
572 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5237
573 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5238
574 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5239
575 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5240
576 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5241
577 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5242
578 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5243
579 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5244
580 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5245
581 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5246
582 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5247