## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
6 | 30V DC-2 | 110V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
7 | 30V DC-2 | 110V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
8 | 30V DC-2 | 110V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
9 | 30V DC-2 | 110V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
10 | 30V DC-2 | 110V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
11 | 30V DC-2 | 110V | DC DIST. BOARD | DC load Voltage | AI |  | 0-110V DC | Hard | Transducer | 5005
12 | 30V DC-2 | 110V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
13 | 30V DC-2 | 110V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
14 | SubStation Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
15 | SubStation Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
16 | SubStation Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
17 | SubStation Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
18 | SubStation Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
19 | SubStation Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
20 | Station Transformer | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5008
21 | Station Transformer | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5009
22 | Station Transformer | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5010
23 | Station Transformer | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5011
24 | Station Transformer | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5012
25 | Station Transformer | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5013
26 | Station Transformer | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5014
27 | Transformer 2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
28 | Transformer 2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
29 | Transformer 2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
30 | Transformer 2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
31 | Transformer 2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
32 | Transformer 2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
33 | Transformer 2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
34 | Transformer 2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
35 | Transformer 2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
36 | Transformer 2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
37 | Transformer 2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
38 | Transformer 2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
39 | Transformer 2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
40 | Transformer 2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
41 | Transformer 2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
42 | Transformer 2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
43 | Transformer 2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
44 | Transformer 2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
45 | Transformer 2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
46 | Transformer 2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
47 | Transformer 2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
48 | Transformer 2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
49 | Transformer 2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
50 | Transformer 2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
51 | Transformer 2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
52 | Transformer 2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
53 | Transformer 2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
54 | Transformer 2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
55 | Transformer 2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
56 | Transformer 2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer 2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5015
58 | Transformer 2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5016
59 | Transformer 2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5017
60 | Transformer 2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5018
61 | Transformer 2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5019
62 | Transformer 2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5020
63 | Transformer 2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5021
64 | Transformer 2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5022
65 | Transformer 2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5023
66 | Transformer 2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5024
67 | Transformer 2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5025
68 | Transformer 2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5026
69 | Transformer 2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5027
70 | Transformer 2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5028
71 | Transformer 2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5029
72 | Transformer 2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5030
73 | Transformer 2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5031
74 | Transformer 2 | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
75 | Transformer 2 | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
76 | Transformer 2 | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
77 | Transformer 2 | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
78 | Transformer 2 | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
79 | Transformer 2 | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
80 | Transformer 2 | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
81 | Transformer 2 | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
82 | Transformer 2 | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
83 | Transformer 2 | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
84 | Transformer 2 | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5032
85 | Transformer 2 | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5033
86 | Transformer 2 | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5034
87 | Incomer-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 48
88 | Incomer-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 49
89 | Incomer-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 50
90 | Incomer-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 51
91 | Incomer-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 52
92 | Incomer-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 53
93 | Incomer-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 54
94 | Incomer-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 55
95 | Incomer-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 56
96 | Incomer-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 57
97 | Incomer-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 58
98 | Incomer-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 59
99 | Incomer-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13006
100 | Incomer-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13007
101 | Incomer-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13008
102 | Incomer-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10002
103 | Incomer-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10002
104 | Incomer-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5035
105 | Incomer-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5036
106 | Incomer-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5037
107 | Incomer-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5038
108 | Incomer-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5039
109 | Incomer-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5040
110 | Incomer-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5041
111 | Incomer-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5042
112 | Incomer-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5043
113 | Incomer-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5044
114 | Incomer-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5045
115 | Incomer-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5046
116 | Incomer-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5047
117 | Incomer-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5048
118 | Incomer-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5049
119 | Incomer-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5050
120 | Incomer-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5051
121 | Incomer-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5052
122 | Incomer-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5053
123 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER DS ON | SPI |  |  | Hard | CMR | 60 |  |  |  | Applicable only for GIS as a additional.
124 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER DS OFF | SPI |  |  | Hard | CMR | 61 |  |  |  | Applicable only for GIS as a additional.
125 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER DS ON | SPC |  |  | Hard | HDR | 13009 |  |  |  | Applicable only for GIS as a additional.
126 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER DS OFF | SPC |  |  | Hard | HDR | 13010 |  |  |  | Applicable only for GIS as a additional.
127 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH ON | SPI |  |  | Hard | CMR | 62 |  |  |  | Applicable only for GIS as a additional.
128 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH OFF | SPI |  |  | Hard | CMR | 63 |  |  |  | Applicable only for GIS as a additional.
129 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH ON | SPC |  |  | Hard | HDR | 13011 |  |  |  | Applicable only for GIS as a additional.
130 | Bus-Riser | 33kV | 33KV BUS RISER | BUS RISER EARTH SWITCH OFF | SPC |  |  | Hard | HDR | 13012 |  |  |  | Applicable only for GIS as a additional.
131 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch on | SPI |  |  | Soft | IED | 64 |  |  |  | Applicable only for GIS as a additional.
132 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch off | SPI |  |  | Soft | IED | 65 |  |  |  | Applicable only for GIS as a additional.
133 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch on | SPI |  |  | Soft | IED | 66 |  |  |  | Applicable only for GIS as a additional.
134 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch off | SPI |  |  | Soft | IED | 67 |  |  |  | Applicable only for GIS as a additional.
135 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Busbar chamber gas pressure low | SPI |  |  | Soft | IED | 68 |  |  |  | Applicable only for GIS as a additional.
136 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Circuit breaker chamber gas pressure low | SPI |  |  | Soft | IED | 69 |  |  |  | Applicable only for GIS as a additional.
137 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch on | SPC |  |  | Hard | HDR | 13013 |  |  |  | Applicable only for GIS as a additional.
138 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch off | SPC |  |  | Hard | HDR | 13014 |  |  |  | Applicable only for GIS as a additional.
139 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch on | SPC |  |  | Hard | HDR | 13015 |  |  |  | Applicable only for GIS as a additional.
140 | Bus Coupler | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch off | SPC |  |  | Hard | HDR | 13016 |  |  |  | Applicable only for GIS as a additional.
141 | Bus Coupler | 33kV | 33KV BC | Earth Switch2 on | SPI |  |  | Soft | IED | 70 |  |  |  | Applicable only for GIS as a additional.
142 | Bus Coupler | 33kV | 33KV BC | Earth Switch2 off | SPI |  |  | Soft | IED | 71 |  |  |  | Applicable only for GIS as a additional.
143 | Bus Coupler | 33kV | 33KV BC | Earth Switch2 on | SPC |  |  | Hard | HDR | 13017 |  |  |  | Applicable only for GIS as a additional.
144 | Bus Coupler | 33kV | 33KV BC | Earth Switch2 off | SPC |  |  | Hard | HDR | 13018 |  |  |  | Applicable only for GIS as a additional.
145 | Incomer-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 72
146 | Incomer-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 73
147 | Incomer-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 74
148 | Incomer-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 75
149 | Incomer-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 76
150 | Incomer-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 77
151 | Incomer-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 78
152 | Incomer-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 79
153 | Incomer-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 80
154 | Incomer-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 81
155 | Incomer-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 82
156 | Incomer-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 83
157 | Incomer-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13019
158 | Incomer-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13020
159 | Incomer-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13021
160 | Incomer-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10003
161 | Incomer-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10003
162 | Incomer-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5054
163 | Incomer-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5055
164 | Incomer-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5056
165 | Incomer-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5057
166 | Incomer-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5058
167 | Incomer-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5059
168 | Incomer-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5060
169 | Incomer-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5061
170 | Incomer-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5062
171 | Incomer-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5063
172 | Incomer-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5064
173 | Incomer-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5065
174 | Incomer-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5066
175 | Incomer-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5067
176 | Incomer-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5068
177 | Incomer-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5069
178 | Incomer-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5070
179 | Incomer-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5071
180 | Incomer-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5072
181 | Transformer -1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 84
182 | Transformer -1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 85
183 | Transformer -1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 86
184 | Transformer -1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 87
185 | Transformer -1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 88
186 | Transformer -1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 89
187 | Transformer -1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 90
188 | Transformer -1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 91
189 | Transformer -1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 92
190 | Transformer -1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 93
191 | Transformer -1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 94
192 | Transformer -1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 95
193 | Transformer -1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 96
194 | Transformer -1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 97
195 | Transformer -1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 98
196 | Transformer -1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 99
197 | Transformer -1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 100
198 | Transformer -1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 101
199 | Transformer -1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 102
200 | Transformer -1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 103
201 | Transformer -1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 104
202 | Transformer -1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 105
203 | Transformer -1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 106
204 | Transformer -1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 107
205 | Transformer -1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13022
206 | Transformer -1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13023
207 | Transformer -1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13024
208 | Transformer -1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13025
209 | Transformer -1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
210 | Transformer -1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
211 | Transformer -1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5073
212 | Transformer -1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5074
213 | Transformer -1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5075
214 | Transformer -1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5076
215 | Transformer -1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5077
216 | Transformer -1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5078
217 | Transformer -1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5079
218 | Transformer -1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5080
219 | Transformer -1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5081
220 | Transformer -1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5082
221 | Transformer -1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5083
222 | Transformer -1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5084
223 | Transformer -1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5085
224 | Transformer -1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5086
225 | Transformer -1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5087
226 | Transformer -1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5088
227 | Transformer -1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5089
228 | Transformer -1 | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 108
229 | Transformer -1 | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 109
230 | Transformer -1 | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 110 |  |  |  | AC CMR to be used
231 | Transformer -1 | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 111
232 | Transformer -1 | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 112
233 | Transformer -1 | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 113
234 | Transformer -1 | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 114
235 | Transformer -1 | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 115
236 | Transformer -1 | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13026
237 | Transformer -1 | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13027
238 | Transformer -1 | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5090
239 | Transformer -1 | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5091
240 | Transformer -1 | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5092
241 | Rajarhat IT Park | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 116
242 | Rajarhat IT Park | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 117
243 | Rajarhat IT Park | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 118
244 | Rajarhat IT Park | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 119
245 | Rajarhat IT Park | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 120
246 | Rajarhat IT Park | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 121
247 | Rajarhat IT Park | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 122
248 | Rajarhat IT Park | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 123
249 | Rajarhat IT Park | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 124
250 | Rajarhat IT Park | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 125
251 | Rajarhat IT Park | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 126
252 | Rajarhat IT Park | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 127
253 | Rajarhat IT Park | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13028
254 | Rajarhat IT Park | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13029
255 | Rajarhat IT Park | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13030
256 | Rajarhat IT Park | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
257 | Rajarhat IT Park | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
258 | Rajarhat IT Park | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5093
259 | Rajarhat IT Park | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5094
260 | Rajarhat IT Park | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5095
261 | Rajarhat IT Park | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5096
262 | Rajarhat IT Park | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5097
263 | Rajarhat IT Park | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5098
264 | Rajarhat IT Park | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5099
265 | Rajarhat IT Park | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5100
266 | Rajarhat IT Park | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5101
267 | Rajarhat IT Park | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5102
268 | Rajarhat IT Park | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5103
269 | Rajarhat IT Park | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5104
270 | Rajarhat IT Park | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5105
271 | Rajarhat IT Park | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5106
272 | Rajarhat IT Park | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5107
273 | Rajarhat IT Park | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5108
274 | Rajarhat IT Park | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5109
275 | Rajarhat IT Park | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5110
276 | Rajarhat IT Park | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5111
277 | 11kV Incomer 1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 128
278 | 11kV Incomer 1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 129
279 | 11kV Incomer 1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 130
280 | 11kV Incomer 1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 131
281 | 11kV Incomer 1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 132
282 | 11kV Incomer 1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 133
283 | 11kV Incomer 1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 134
284 | 11kV Incomer 1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 135
285 | 11kV Incomer 1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 136
286 | 11kV Incomer 1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 137
287 | 11kV Incomer 1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 138
288 | 11kV Incomer 1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 139
289 | 11kV Incomer 1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 140
290 | 11kV Incomer 1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
291 | 11kV Incomer 1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
292 | 11kV Incomer 1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13031
293 | 11kV Incomer 1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13032
294 | 11kV Incomer 1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13033
295 | 11kV Incomer 1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5112
296 | 11kV Incomer 1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5113
297 | 11kV Incomer 1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5114
298 | 11kV Incomer 1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5115
299 | 11kV Incomer 1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5116
300 | 11kV Incomer 1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5117
301 | 11kV Incomer 1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5118
302 | 11kV Incomer 1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5119
303 | 11kV Incomer 1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5120
304 | 11kV Incomer 1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5121
305 | 11kV Incomer 1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5122
306 | 11kV Incomer 1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5123
307 | 11kV Incomer 1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5124
308 | 11kV Incomer 1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5125
309 | 11kV Incomer 1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5126
310 | 11kV Incomer 1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5127
311 | 11kV Incomer 1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5128
312 | PS Qube | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 141
313 | PS Qube | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 142
314 | PS Qube | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 143
315 | PS Qube | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 144
316 | PS Qube | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 145
317 | PS Qube | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 146
318 | PS Qube | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 147
319 | PS Qube | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 148
320 | PS Qube | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 149
321 | PS Qube | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 150
322 | PS Qube | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 151
323 | PS Qube | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 152
324 | PS Qube | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 153
325 | PS Qube | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 154
326 | PS Qube | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
327 | PS Qube | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
328 | PS Qube | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13034
329 | PS Qube | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13035
330 | PS Qube | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13036
331 | PS Qube | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5129
332 | PS Qube | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5130
333 | PS Qube | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5131
334 | PS Qube | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5132
335 | PS Qube | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5133
336 | PS Qube | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5134
337 | PS Qube | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5135
338 | PS Qube | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5136
339 | PS Qube | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5137
340 | PS Qube | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5138
341 | PS Qube | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5139
342 | PS Qube | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5140
343 | PS Qube | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5141
344 | PS Qube | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5142
345 | PS Qube | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5143
346 | PS Qube | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5144
347 | PS Qube | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5145
348 | IAS Housing | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 155
349 | IAS Housing | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 156
350 | IAS Housing | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 157
351 | IAS Housing | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 158
352 | IAS Housing | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 159
353 | IAS Housing | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 160
354 | IAS Housing | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 161
355 | IAS Housing | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 162
356 | IAS Housing | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 163
357 | IAS Housing | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 164
358 | IAS Housing | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 165
359 | IAS Housing | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 166
360 | IAS Housing | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 167
361 | IAS Housing | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 168
362 | IAS Housing | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
363 | IAS Housing | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
364 | IAS Housing | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13037
365 | IAS Housing | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13038
366 | IAS Housing | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13039
367 | IAS Housing | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5146
368 | IAS Housing | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5147
369 | IAS Housing | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5148
370 | IAS Housing | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5149
371 | IAS Housing | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5150
372 | IAS Housing | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5151
373 | IAS Housing | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5152
374 | IAS Housing | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5153
375 | IAS Housing | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5154
376 | IAS Housing | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5155
377 | IAS Housing | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5156
378 | IAS Housing | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5157
379 | IAS Housing | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5158
380 | IAS Housing | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5159
381 | IAS Housing | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5160
382 | IAS Housing | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5161
383 | IAS Housing | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5162
384 | DSS-V AA-II | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 169
385 | DSS-V AA-II | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 170
386 | DSS-V AA-II | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 171
387 | DSS-V AA-II | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 172
388 | DSS-V AA-II | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 173
389 | DSS-V AA-II | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 174
390 | DSS-V AA-II | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 175
391 | DSS-V AA-II | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 176
392 | DSS-V AA-II | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 177
393 | DSS-V AA-II | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 178
394 | DSS-V AA-II | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 179
395 | DSS-V AA-II | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 180
396 | DSS-V AA-II | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 181
397 | DSS-V AA-II | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 182
398 | DSS-V AA-II | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
399 | DSS-V AA-II | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
400 | DSS-V AA-II | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13040
401 | DSS-V AA-II | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13041
402 | DSS-V AA-II | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13042
403 | DSS-V AA-II | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5163
404 | DSS-V AA-II | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5164
405 | DSS-V AA-II | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5165
406 | DSS-V AA-II | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5166
407 | DSS-V AA-II | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5167
408 | DSS-V AA-II | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5168
409 | DSS-V AA-II | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5169
410 | DSS-V AA-II | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5170
411 | DSS-V AA-II | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5171
412 | DSS-V AA-II | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5172
413 | DSS-V AA-II | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5173
414 | DSS-V AA-II | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5174
415 | DSS-V AA-II | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5175
416 | DSS-V AA-II | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5176
417 | DSS-V AA-II | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5177
418 | DSS-V AA-II | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5178
419 | DSS-V AA-II | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5179
420 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 183
421 | Bus Coupler | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 184
422 | Bus Coupler | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 185
423 | Bus Coupler | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 186
424 | Bus Coupler | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 187
425 | Bus Coupler | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 188
426 | Bus Coupler | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 189
427 | Bus Coupler | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 190 |  |  |  | AC CMR to be used
428 | Bus Coupler | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 191
429 | Bus Coupler | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 192
430 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10010
431 | Bus Coupler | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10010
432 | 11kV Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 193
433 | 11kV Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 194
434 | 11kV Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 195
435 | 11kV Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 196
436 | 11kV Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 197
437 | 11kV Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 198
438 | 11kV Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 199
439 | 11kV Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 200
440 | 11kV Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 201
441 | 11kV Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 202
442 | 11kV Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 203
443 | 11kV Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 204
444 | 11kV Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 205
445 | 11kV Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
446 | 11kV Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
447 | 11kV Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13043
448 | 11kV Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13044
449 | 11kV Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13045
450 | 11kV Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5180
451 | 11kV Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5181
452 | 11kV Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5182
453 | 11kV Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5183
454 | 11kV Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5184
455 | 11kV Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5185
456 | 11kV Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5186
457 | 11kV Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5187
458 | 11kV Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5188
459 | 11kV Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5189
460 | 11kV Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5190
461 | 11kV Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5191
462 | 11kV Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5192
463 | 11kV Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5193
464 | 11kV Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5194
465 | 11kV Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5195
466 | 11kV Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5196
467 | DSS-IV AA-II | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 206
468 | DSS-IV AA-II | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 207
469 | DSS-IV AA-II | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 208
470 | DSS-IV AA-II | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 209
471 | DSS-IV AA-II | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 210
472 | DSS-IV AA-II | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 211
473 | DSS-IV AA-II | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 212
474 | DSS-IV AA-II | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 213
475 | DSS-IV AA-II | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 214
476 | DSS-IV AA-II | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 215
477 | DSS-IV AA-II | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 216
478 | DSS-IV AA-II | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 217
479 | DSS-IV AA-II | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 218
480 | DSS-IV AA-II | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 219
481 | DSS-IV AA-II | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
482 | DSS-IV AA-II | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
483 | DSS-IV AA-II | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13046
484 | DSS-IV AA-II | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13047
485 | DSS-IV AA-II | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13048
486 | DSS-IV AA-II | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5197
487 | DSS-IV AA-II | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5198
488 | DSS-IV AA-II | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5199
489 | DSS-IV AA-II | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5200
490 | DSS-IV AA-II | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5201
491 | DSS-IV AA-II | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5202
492 | DSS-IV AA-II | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5203
493 | DSS-IV AA-II | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5204
494 | DSS-IV AA-II | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5205
495 | DSS-IV AA-II | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5206
496 | DSS-IV AA-II | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5207
497 | DSS-IV AA-II | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5208
498 | DSS-IV AA-II | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5209
499 | DSS-IV AA-II | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5210
500 | DSS-IV AA-II | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5211
501 | DSS-IV AA-II | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5212
502 | DSS-IV AA-II | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5213
503 | IPS Housing | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 220
504 | IPS Housing | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 221
505 | IPS Housing | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 222
506 | IPS Housing | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 223
507 | IPS Housing | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 224
508 | IPS Housing | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 225
509 | IPS Housing | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 226
510 | IPS Housing | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 227
511 | IPS Housing | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 228
512 | IPS Housing | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 229
513 | IPS Housing | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 230
514 | IPS Housing | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 231
515 | IPS Housing | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 232
516 | IPS Housing | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 233
517 | IPS Housing | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
518 | IPS Housing | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
519 | IPS Housing | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13049
520 | IPS Housing | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13050
521 | IPS Housing | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13051
522 | IPS Housing | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5214
523 | IPS Housing | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5215
524 | IPS Housing | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5216
525 | IPS Housing | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5217
526 | IPS Housing | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5218
527 | IPS Housing | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5219
528 | IPS Housing | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5220
529 | IPS Housing | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5221
530 | IPS Housing | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5222
531 | IPS Housing | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5223
532 | IPS Housing | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5224
533 | IPS Housing | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5225
534 | IPS Housing | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5226
535 | IPS Housing | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5227
536 | IPS Housing | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5228
537 | IPS Housing | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5229
538 | IPS Housing | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5230
539 | DSS-I New RMU | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 234
540 | DSS-I New RMU | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 235
541 | DSS-I New RMU | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 236
542 | DSS-I New RMU | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 237
543 | DSS-I New RMU | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 238
544 | DSS-I New RMU | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 239
545 | DSS-I New RMU | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 240
546 | DSS-I New RMU | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 241
547 | DSS-I New RMU | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 242
548 | DSS-I New RMU | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 243
549 | DSS-I New RMU | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 244
550 | DSS-I New RMU | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 245
551 | DSS-I New RMU | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 246
552 | DSS-I New RMU | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 247
553 | DSS-I New RMU | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
554 | DSS-I New RMU | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
555 | DSS-I New RMU | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13052
556 | DSS-I New RMU | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13053
557 | DSS-I New RMU | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13054
558 | DSS-I New RMU | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5231
559 | DSS-I New RMU | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5232
560 | DSS-I New RMU | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5233
561 | DSS-I New RMU | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5234
562 | DSS-I New RMU | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5235
563 | DSS-I New RMU | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5236
564 | DSS-I New RMU | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5237
565 | DSS-I New RMU | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5238
566 | DSS-I New RMU | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5239
567 | DSS-I New RMU | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5240
568 | DSS-I New RMU | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5241
569 | DSS-I New RMU | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5242
570 | DSS-I New RMU | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5243
571 | DSS-I New RMU | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5244
572 | DSS-I New RMU | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5245
573 | DSS-I New RMU | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5246
574 | DSS-I New RMU | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5247