## Signal List
SCADA/Advanced Distribution Management System (DMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V_DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V_DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V_DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V_DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V_DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V_DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V_DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V_DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V_DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V_DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V_DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V_DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V_DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V_DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V_DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V_DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V_DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V_DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V_DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V_DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V_DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | SUBSTATION COMMON |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | Dummy CB | 3000
23 | SUBSTATION COMMON |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | Dummy CB | 10000
24 | SUBSTATION COMMON |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | SUBSTATION COMMON |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | SUBSTATION COMMON |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | SUBSTATION COMMON |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5008
29 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5009
30 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5010
31 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5011
32 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5012
33 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5013
34 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5014
35 | SUKHOBRIST | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 16
36 | SUKHOBRIST | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 17
37 | SUKHOBRIST | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 18
38 | SUKHOBRIST | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 19
39 | SUKHOBRIST | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 20
40 | SUKHOBRIST | 33kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 21 |  |  |  | For AIS (Indoor) Only
41 | SUKHOBRIST | 33kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 22 |  |  |  | For AIS (Indoor) Only
42 | SUKHOBRIST | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 23
43 | SUKHOBRIST | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 24
44 | SUKHOBRIST | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 25
45 | SUKHOBRIST | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 26
46 | SUKHOBRIST | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 27
47 | SUKHOBRIST | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 28
48 | SUKHOBRIST | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 29
49 | SUKHOBRIST | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13000
50 | SUKHOBRIST | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13001
51 | SUKHOBRIST | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13002
52 | SUKHOBRIST | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10001
53 | SUKHOBRIST | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10001
54 | SUKHOBRIST | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5015
55 | SUKHOBRIST | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5016
56 | SUKHOBRIST | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5017
57 | SUKHOBRIST | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5018
58 | SUKHOBRIST | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5019
59 | SUKHOBRIST | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5020
60 | SUKHOBRIST | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5021
61 | SUKHOBRIST | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5022
62 | SUKHOBRIST | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5023
63 | SUKHOBRIST | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5024
64 | SUKHOBRIST | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5025
65 | SUKHOBRIST | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5026
66 | SUKHOBRIST | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5027
67 | SUKHOBRIST | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5028
68 | SUKHOBRIST | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5029
69 | SUKHOBRIST | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5030
70 | SUKHOBRIST | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5031
71 | SUKHOBRIST | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5032
72 | SUKHOBRIST | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5033
73 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 30
74 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 31
75 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 32
76 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 33
77 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 34
78 | Transformer-1 | 33kV | Transformer | Test Position | SPI |  |  | Hard | CMR | 35 |  |  |  | Applicable for AIS(indoor)
79 | Transformer-1 | 33kV | Transformer | Service Position | SPI |  |  | Hard | CMR | 36 |  |  |  | Applicable for AIS(indoor)
80 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 37
81 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 38
82 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 39
83 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 40
84 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 41
85 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 42
86 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 43
87 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 44
88 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 45
89 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 46
90 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 47
91 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 48
92 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 49
93 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 50
94 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 51
95 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 52
96 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 53
97 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 54
98 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 55
99 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13003
100 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13004
101 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13005
102 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13006
103 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
104 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
105 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5034
106 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5035
107 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5036
108 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5037
109 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5038
110 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5039
111 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5040
112 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5041
113 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5042
114 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5043
115 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5044
116 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5045
117 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5046
118 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5047
119 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5048
120 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5049
121 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5050
122 | Transformer-1(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 56
123 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 57
124 | Transformer-1(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 58 |  |  |  | AC CMR to be used
125 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 59
126 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 60
127 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 61
128 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 62
129 | Transformer-1(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 63
130 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13007
131 | Transformer-1(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13008
132 | Transformer-1(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5051
133 | Transformer-1(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5052
134 | Transformer-1(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5053
135 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch on | SPI |  |  | Soft | IED | 64 |  |  |  | Applicable only for GIS as a additional.
136 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch off | SPI |  |  | Soft | IED | 65 |  |  |  | Applicable only for GIS as a additional.
137 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch on | SPI |  |  | Soft | IED | 66 |  |  |  | Applicable only for GIS as a additional.
138 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch off | SPI |  |  | Soft | IED | 67 |  |  |  | Applicable only for GIS as a additional.
139 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Busbar chamber gas pressure low | SPI |  |  | Soft | IED | 68 |  |  |  | Applicable only for GIS as a additional.
140 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Circuit breaker chamber gas pressure low | SPI |  |  | Soft | IED | 69 |  |  |  | Applicable only for GIS as a additional.
141 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch on | SPC |  |  | Hard | HDR | 13009 |  |  |  | Applicable only for GIS as a additional.
142 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Disconnecting switch off | SPC |  |  | Hard | HDR | 13010 |  |  |  | Applicable only for GIS as a additional.
143 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch on | SPC |  |  | Hard | HDR | 13011 |  |  |  | Applicable only for GIS as a additional.
144 | BUSCOUPLER | 33kV | 33kV BC/OG/IC/TR/STR | Earth switch off | SPC |  |  | Hard | HDR | 13012 |  |  |  | Applicable only for GIS as a additional.
145 | BUSCOUPLER | 33kV | 33KV BC | Earth Switch2 on | SPI |  |  | Soft | IED | 70 |  |  |  | Applicable only for GIS as a additional.
146 | BUSCOUPLER | 33kV | 33KV BC | Earth Switch2 off | SPI |  |  | Soft | IED | 71 |  |  |  | Applicable only for GIS as a additional.
147 | BUSCOUPLER | 33kV | 33KV BC | Earth Switch2 on | SPC |  |  | Hard | HDR | 13013 |  |  |  | Applicable only for GIS as a additional.
148 | BUSCOUPLER | 33kV | 33KV BC | Earth Switch2 off | SPC |  |  | Hard | HDR | 13014 |  |  |  | Applicable only for GIS as a additional.
149 | 33KV_SPARE | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 72
150 | 33KV_SPARE | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 73
151 | 33KV_SPARE | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 74
152 | 33KV_SPARE | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 75
153 | 33KV_SPARE | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 76
154 | 33KV_SPARE | 33kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 77 |  |  |  | For AIS (Indoor) Only
155 | 33KV_SPARE | 33kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 78 |  |  |  | For AIS (Indoor) Only
156 | 33KV_SPARE | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 79
157 | 33KV_SPARE | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 80
158 | 33KV_SPARE | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 81
159 | 33KV_SPARE | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 82
160 | 33KV_SPARE | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 83
161 | 33KV_SPARE | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 84
162 | 33KV_SPARE | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 85
163 | 33KV_SPARE | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13015
164 | 33KV_SPARE | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13016
165 | 33KV_SPARE | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13017
166 | 33KV_SPARE | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10003
167 | 33KV_SPARE | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10003
168 | 33KV_SPARE | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5054
169 | 33KV_SPARE | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5055
170 | 33KV_SPARE | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5056
171 | 33KV_SPARE | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5057
172 | 33KV_SPARE | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5058
173 | 33KV_SPARE | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5059
174 | 33KV_SPARE | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5060
175 | 33KV_SPARE | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5061
176 | 33KV_SPARE | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5062
177 | 33KV_SPARE | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5063
178 | 33KV_SPARE | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5064
179 | 33KV_SPARE | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5065
180 | 33KV_SPARE | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5066
181 | 33KV_SPARE | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5067
182 | 33KV_SPARE | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5068
183 | 33KV_SPARE | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5069
184 | 33KV_SPARE | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5070
185 | 33KV_SPARE | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5071
186 | 33KV_SPARE | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5072
187 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 86
188 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 87
189 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 88
190 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 89
191 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 90
192 | Transformer-2 | 33kV | Transformer | Test Position | SPI |  |  | Hard | CMR | 91 |  |  |  | Applicable for AIS(indoor)
193 | Transformer-2 | 33kV | Transformer | Service Position | SPI |  |  | Hard | CMR | 92 |  |  |  | Applicable for AIS(indoor)
194 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 93
195 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 94
196 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 95
197 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 96
198 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 97
199 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 98
200 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 99
201 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 100
202 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 101
203 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 102
204 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 103
205 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 104
206 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 105
207 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 106
208 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 107
209 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 108
210 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 109
211 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 110
212 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 111
213 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
214 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
215 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
216 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
217 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
218 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
219 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5073
220 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5074
221 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5075
222 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5076
223 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5077
224 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5078
225 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5079
226 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5080
227 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5081
228 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5082
229 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5083
230 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5084
231 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5085
232 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5086
233 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5087
234 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5088
235 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5089
236 | Transformer-2(RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 112
237 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 113
238 | Transformer-2(RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 114 |  |  |  | AC CMR to be used
239 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 115
240 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 116
241 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 117
242 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 118
243 | Transformer-2(RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 119
244 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
245 | Transformer-2(RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
246 | Transformer-2(RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5090
247 | Transformer-2(RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5091
248 | Transformer-2(RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5092
249 | DLF S/S | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 120
250 | DLF S/S | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 121
251 | DLF S/S | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 122
252 | DLF S/S | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 123
253 | DLF S/S | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 124
254 | DLF S/S | 33kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 125 |  |  |  | For AIS (Indoor) Only
255 | DLF S/S | 33kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 126 |  |  |  | For AIS (Indoor) Only
256 | DLF S/S | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 127
257 | DLF S/S | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 128
258 | DLF S/S | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 129
259 | DLF S/S | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 130
260 | DLF S/S | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 131
261 | DLF S/S | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 132
262 | DLF S/S | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 133
263 | DLF S/S | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
264 | DLF S/S | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
265 | DLF S/S | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
266 | DLF S/S | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
267 | DLF S/S | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
268 | DLF S/S | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5093
269 | DLF S/S | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5094
270 | DLF S/S | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5095
271 | DLF S/S | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5096
272 | DLF S/S | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5097
273 | DLF S/S | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5098
274 | DLF S/S | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5099
275 | DLF S/S | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5100
276 | DLF S/S | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5101
277 | DLF S/S | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5102
278 | DLF S/S | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5103
279 | DLF S/S | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5104
280 | DLF S/S | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5105
281 | DLF S/S | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5106
282 | DLF S/S | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5107
283 | DLF S/S | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5108
284 | DLF S/S | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5109
285 | DLF S/S | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5110
286 | DLF S/S | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5111
287 | Incomer-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 134
288 | Incomer-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 135
289 | Incomer-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 136
290 | Incomer-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 137
291 | Incomer-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 138
292 | Incomer-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 139
293 | Incomer-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 140
294 | Incomer-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 141
295 | Incomer-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 142
296 | Incomer-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 143
297 | Incomer-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 144
298 | Incomer-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 145
299 | Incomer-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 146
300 | Incomer-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
301 | Incomer-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
302 | Incomer-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
303 | Incomer-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13028
304 | Incomer-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13029
305 | Incomer-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5112
306 | Incomer-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5113
307 | Incomer-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5114
308 | Incomer-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5115
309 | Incomer-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5116
310 | Incomer-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5117
311 | Incomer-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5118
312 | Incomer-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5119
313 | Incomer-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5120
314 | Incomer-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5121
315 | Incomer-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5122
316 | Incomer-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5123
317 | Incomer-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5124
318 | Incomer-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5125
319 | Incomer-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5126
320 | Incomer-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5127
321 | Incomer-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5128
322 | DSS4 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 147
323 | DSS4 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 148
324 | DSS4 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 149
325 | DSS4 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 150
326 | DSS4 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 151
327 | DSS4 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 152
328 | DSS4 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 153
329 | DSS4 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 154
330 | DSS4 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 155
331 | DSS4 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 156
332 | DSS4 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 157
333 | DSS4 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 158
334 | DSS4 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 159
335 | DSS4 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 160
336 | DSS4 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
337 | DSS4 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
338 | DSS4 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
339 | DSS4 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
340 | DSS4 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13032
341 | DSS4 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5129
342 | DSS4 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5130
343 | DSS4 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5131
344 | DSS4 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5132
345 | DSS4 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5133
346 | DSS4 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5134
347 | DSS4 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5135
348 | DSS4 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5136
349 | DSS4 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5137
350 | DSS4 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5138
351 | DSS4 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5139
352 | DSS4 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5140
353 | DSS4 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5141
354 | DSS4 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5142
355 | DSS4 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5143
356 | DSS4 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5144
357 | DSS4 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5145
358 | DSS2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 161
359 | DSS2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 162
360 | DSS2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 163
361 | DSS2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 164
362 | DSS2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 165
363 | DSS2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 166
364 | DSS2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 167
365 | DSS2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 168
366 | DSS2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 169
367 | DSS2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 170
368 | DSS2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 171
369 | DSS2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 172
370 | DSS2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 173
371 | DSS2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 174
372 | DSS2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
373 | DSS2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
374 | DSS2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
375 | DSS2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
376 | DSS2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13035
377 | DSS2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5146
378 | DSS2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5147
379 | DSS2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5148
380 | DSS2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5149
381 | DSS2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5150
382 | DSS2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5151
383 | DSS2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5152
384 | DSS2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5153
385 | DSS2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5154
386 | DSS2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5155
387 | DSS2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5156
388 | DSS2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5157
389 | DSS2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5158
390 | DSS2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5159
391 | DSS2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5160
392 | DSS2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5161
393 | DSS2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5162
394 | WBTC EV Charging | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 175
395 | WBTC EV Charging | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 176
396 | WBTC EV Charging | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 177
397 | WBTC EV Charging | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 178
398 | WBTC EV Charging | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 179
399 | WBTC EV Charging | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 180
400 | WBTC EV Charging | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 181
401 | WBTC EV Charging | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 182
402 | WBTC EV Charging | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 183
403 | WBTC EV Charging | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 184
404 | WBTC EV Charging | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 185
405 | WBTC EV Charging | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 186
406 | WBTC EV Charging | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 187
407 | WBTC EV Charging | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 188
408 | WBTC EV Charging | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
409 | WBTC EV Charging | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
410 | WBTC EV Charging | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
411 | WBTC EV Charging | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
412 | WBTC EV Charging | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13038
413 | WBTC EV Charging | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5163
414 | WBTC EV Charging | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5164
415 | WBTC EV Charging | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5165
416 | WBTC EV Charging | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5166
417 | WBTC EV Charging | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5167
418 | WBTC EV Charging | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5168
419 | WBTC EV Charging | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5169
420 | WBTC EV Charging | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5170
421 | WBTC EV Charging | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5171
422 | WBTC EV Charging | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5172
423 | WBTC EV Charging | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5173
424 | WBTC EV Charging | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5174
425 | WBTC EV Charging | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5175
426 | WBTC EV Charging | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5176
427 | WBTC EV Charging | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5177
428 | WBTC EV Charging | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5178
429 | WBTC EV Charging | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5179
430 | BUSCOUPLER | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 189
431 | BUSCOUPLER | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 190
432 | BUSCOUPLER | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 191
433 | BUSCOUPLER | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 192
434 | BUSCOUPLER | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 193
435 | BUSCOUPLER | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 194
436 | BUSCOUPLER | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 195
437 | BUSCOUPLER | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 196 |  |  |  | AC CMR to be used
438 | BUSCOUPLER | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 197
439 | BUSCOUPLER | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 198
440 | BUSCOUPLER | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10010
441 | BUSCOUPLER | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10010
442 | DSS-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 199
443 | DSS-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 200
444 | DSS-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 201
445 | DSS-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 202
446 | DSS-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 203
447 | DSS-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 204
448 | DSS-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 205
449 | DSS-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 206
450 | DSS-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 207
451 | DSS-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 208
452 | DSS-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 209
453 | DSS-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 210
454 | DSS-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 211
455 | DSS-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 212
456 | DSS-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
457 | DSS-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
458 | DSS-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
459 | DSS-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
460 | DSS-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13041
461 | DSS-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5180
462 | DSS-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5181
463 | DSS-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5182
464 | DSS-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5183
465 | DSS-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5184
466 | DSS-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5185
467 | DSS-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5186
468 | DSS-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5187
469 | DSS-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5188
470 | DSS-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5189
471 | DSS-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5190
472 | DSS-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5191
473 | DSS-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5192
474 | DSS-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5193
475 | DSS-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5194
476 | DSS-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5195
477 | DSS-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5196
478 | Bulk Utility | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 213
479 | Bulk Utility | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 214
480 | Bulk Utility | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 215
481 | Bulk Utility | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 216
482 | Bulk Utility | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 217
483 | Bulk Utility | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 218
484 | Bulk Utility | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 219
485 | Bulk Utility | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 220
486 | Bulk Utility | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 221
487 | Bulk Utility | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 222
488 | Bulk Utility | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 223
489 | Bulk Utility | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 224
490 | Bulk Utility | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 225
491 | Bulk Utility | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 226
492 | Bulk Utility | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
493 | Bulk Utility | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
494 | Bulk Utility | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
495 | Bulk Utility | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
496 | Bulk Utility | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
497 | Bulk Utility | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5197
498 | Bulk Utility | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5198
499 | Bulk Utility | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5199
500 | Bulk Utility | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5200
501 | Bulk Utility | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5201
502 | Bulk Utility | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5202
503 | Bulk Utility | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5203
504 | Bulk Utility | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5204
505 | Bulk Utility | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5205
506 | Bulk Utility | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5206
507 | Bulk Utility | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5207
508 | Bulk Utility | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5208
509 | Bulk Utility | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5209
510 | Bulk Utility | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5210
511 | Bulk Utility | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5211
512 | Bulk Utility | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5212
513 | Bulk Utility | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5213
514 | Incomer-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 227
515 | Incomer-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 228
516 | Incomer-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 229
517 | Incomer-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 230
518 | Incomer-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 231
519 | Incomer-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 232
520 | Incomer-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 233
521 | Incomer-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 234
522 | Incomer-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 235
523 | Incomer-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 236
524 | Incomer-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 237
525 | Incomer-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 238
526 | Incomer-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 239
527 | Incomer-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
528 | Incomer-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
529 | Incomer-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
530 | Incomer-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13046
531 | Incomer-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13047
532 | Incomer-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5214
533 | Incomer-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5215
534 | Incomer-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5216
535 | Incomer-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5217
536 | Incomer-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5218
537 | Incomer-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5219
538 | Incomer-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5220
539 | Incomer-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5221
540 | Incomer-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5222
541 | Incomer-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5223
542 | Incomer-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5224
543 | Incomer-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5225
544 | Incomer-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5226
545 | Incomer-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5227
546 | Incomer-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5228
547 | Incomer-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5229
548 | Incomer-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5230