## Signal List
SCADA/Advanced Distribution Management System (ADMS)
SL.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | DUMMY CB | 3000
23 | Sub-Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | DUMMY CB | 10000
24 | Sub-Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Weather Sensor |  | Weather(DOC) | Rain Fall | AI |  |  | Hard | Sensor | 5008
29 | Weather Sensor |  | Weather(DOC) | Wind Speed | AI |  |  | Hard | Sensor | 5009
30 | Weather Sensor |  | Weather(DOC) | Wind Direction | AI |  |  | Hard | Sensor | 5010
31 | Weather Sensor |  | Weather(DOC) | Humidity | AI |  |  | Hard | Sensor | 5011
32 | Weather Sensor |  | Weather(DOC) | Temperature | AI |  |  | Hard | Sensor | 5012
33 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
34 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
35 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
36 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
37 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
38 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
39 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
40 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
41 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
42 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
43 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
44 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
45 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
46 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
47 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
48 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
49 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
50 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
51 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
52 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
53 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
54 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
55 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
56 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
57 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
58 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
59 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
60 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
61 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
62 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
63 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5025
76 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5026
77 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5027
78 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5028
79 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5029
80 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
82 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
86 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
87 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
88 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
89 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
90 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5030
91 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5031
92 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5032
93 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
94 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
95 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
96 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
97 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
98 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
99 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
100 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
101 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
102 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
103 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
104 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
105 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
106 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
107 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
108 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
109 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
110 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
111 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
112 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
113 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
114 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
115 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
116 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
117 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
118 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
119 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
120 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
121 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
122 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
123 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5045
136 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5046
137 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5047
138 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5048
139 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5049
140 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
142 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
146 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
147 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
148 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
149 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
150 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5050
151 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5051
152 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5052
153 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 80
154 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 81
155 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
156 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
157 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
158 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
159 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
160 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
161 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
162 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
163 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
164 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
165 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
166 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
167 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
168 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
169 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
170 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
171 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
172 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
173 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
174 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
175 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
176 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
177 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
178 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
179 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
180 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
181 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
182 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
183 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5065
196 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5066
197 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5067
198 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5068
199 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5069
200 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
202 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
206 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
207 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
208 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
209 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
210 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5070
211 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5071
212 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5072
213 | Transformer-4 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 112
214 | Transformer-4 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 113
215 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 114
216 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 115
217 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 116
218 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 117
219 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 118
220 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 119
221 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 120
222 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 121
223 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 122
224 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 123
225 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 124
226 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 125
227 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 126
228 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 127
229 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 128
230 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 129
231 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 130
232 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 131
233 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 132
234 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 133
235 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 134
236 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 135
237 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
238 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
239 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
240 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
241 | Transformer-4 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
242 | Transformer-4 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
243 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5073
244 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5074
245 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5075
246 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5076
247 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5077
248 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5078
249 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5079
250 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5080
251 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5081
252 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5082
253 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5083
254 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5084
255 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5085
256 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5086
257 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5087
258 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5088
259 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5089
260 | Transformer-4 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 136
261 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 137
262 | Transformer-4 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 138 |  |  |  | AC CMR to be used
263 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 139
264 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 140
265 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 141
266 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 142
267 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 143
268 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
269 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
270 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5090
271 | Transformer-4 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5091
272 | Transformer-4 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5092
273 | Transformer-5 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 144
274 | Transformer-5 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 145
275 | Transformer-5 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 146
276 | Transformer-5 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 147
277 | Transformer-5 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 148
278 | Transformer-5 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 149
279 | Transformer-5 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 150
280 | Transformer-5 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 151
281 | Transformer-5 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 152
282 | Transformer-5 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 153
283 | Transformer-5 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 154
284 | Transformer-5 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 155
285 | Transformer-5 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 156
286 | Transformer-5 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 157
287 | Transformer-5 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 158
288 | Transformer-5 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 159
289 | Transformer-5 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 160
290 | Transformer-5 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 161
291 | Transformer-5 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 162
292 | Transformer-5 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 163
293 | Transformer-5 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 164
294 | Transformer-5 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 165
295 | Transformer-5 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 166
296 | Transformer-5 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 167
297 | Transformer-5 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13024
298 | Transformer-5 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13025
299 | Transformer-5 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13026
300 | Transformer-5 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13027
301 | Transformer-5 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10005
302 | Transformer-5 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10005
303 | Transformer-5 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5093
304 | Transformer-5 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5094
305 | Transformer-5 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5095
306 | Transformer-5 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5096
307 | Transformer-5 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5097
308 | Transformer-5 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5098
309 | Transformer-5 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5099
310 | Transformer-5 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5100
311 | Transformer-5 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5101
312 | Transformer-5 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5102
313 | Transformer-5 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5103
314 | Transformer-5 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5104
315 | Transformer-5 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5105
316 | Transformer-5 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5106
317 | Transformer-5 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5107
318 | Transformer-5 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5108
319 | Transformer-5 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5109
320 | Transformer-5 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 168
321 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 169
322 | Transformer-5 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 170 |  |  |  | AC CMR to be used
323 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 171
324 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 172
325 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 173
326 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 174
327 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 175
328 | Transformer-5 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13028
329 | Transformer-5 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13029
330 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5110
331 | Transformer-5 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5111
332 | Transformer-5 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5112
333 | Bengal Ambuja | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 176
334 | Bengal Ambuja | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 177
335 | Bengal Ambuja | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 178
336 | Bengal Ambuja | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 179
337 | Bengal Ambuja | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 180
338 | Bengal Ambuja | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 181
339 | Bengal Ambuja | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 182
340 | Bengal Ambuja | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 183
341 | Bengal Ambuja | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 184
342 | Bengal Ambuja | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 185
343 | Bengal Ambuja | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 186
344 | Bengal Ambuja | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 187
345 | Bengal Ambuja | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
346 | Bengal Ambuja | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
347 | Bengal Ambuja | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13032
348 | Bengal Ambuja | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
349 | Bengal Ambuja | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
350 | Bengal Ambuja | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5113
351 | Bengal Ambuja | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5114
352 | Bengal Ambuja | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5115
353 | Bengal Ambuja | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5116
354 | Bengal Ambuja | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5117
355 | Bengal Ambuja | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5118
356 | Bengal Ambuja | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5119
357 | Bengal Ambuja | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5120
358 | Bengal Ambuja | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5121
359 | Bengal Ambuja | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5122
360 | Bengal Ambuja | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5123
361 | Bengal Ambuja | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5124
362 | Bengal Ambuja | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5125
363 | Bengal Ambuja | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5126
364 | Bengal Ambuja | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5127
365 | Bengal Ambuja | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5128
366 | Bengal Ambuja | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5129
367 | Bengal Ambuja | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5130
368 | Bengal Ambuja | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5131
369 | Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 188
370 | Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 189
371 | Salt lake fdr-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 190
372 | Salt lake fdr-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 191
373 | Salt lake fdr-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 192
374 | Salt lake fdr-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 193
375 | Salt lake fdr-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 194
376 | Salt lake fdr-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 195
377 | Salt lake fdr-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 196
378 | Salt lake fdr-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 197
379 | Salt lake fdr-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 198
380 | Salt lake fdr-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 199
381 | Salt lake fdr-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
382 | Salt lake fdr-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13034
383 | Salt lake fdr-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13035
384 | Salt lake fdr-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
385 | Salt lake fdr-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
386 | Salt lake fdr-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5132
387 | Salt lake fdr-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5133
388 | Salt lake fdr-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5134
389 | Salt lake fdr-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5135
390 | Salt lake fdr-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5136
391 | Salt lake fdr-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5137
392 | Salt lake fdr-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5138
393 | Salt lake fdr-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5139
394 | Salt lake fdr-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5140
395 | Salt lake fdr-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5141
396 | Salt lake fdr-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5142
397 | Salt lake fdr-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5143
398 | Salt lake fdr-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5144
399 | Salt lake fdr-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5145
400 | Salt lake fdr-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5146
401 | Salt lake fdr-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5147
402 | Salt lake fdr-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5148
403 | Salt lake fdr-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5149
404 | Salt lake fdr-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5150
405 | GIS feeder-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 200
406 | GIS feeder-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 201
407 | GIS feeder-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 202
408 | GIS feeder-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 203
409 | GIS feeder-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 204
410 | GIS feeder-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 205
411 | GIS feeder-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 206
412 | GIS feeder-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 207
413 | GIS feeder-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 208
414 | GIS feeder-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 209
415 | GIS feeder-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 210
416 | GIS feeder-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 211
417 | GIS feeder-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
418 | GIS feeder-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
419 | GIS feeder-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13038
420 | GIS feeder-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
421 | GIS feeder-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
422 | GIS feeder-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5151
423 | GIS feeder-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5152
424 | GIS feeder-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5153
425 | GIS feeder-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5154
426 | GIS feeder-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5155
427 | GIS feeder-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5156
428 | GIS feeder-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5157
429 | GIS feeder-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5158
430 | GIS feeder-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5159
431 | GIS feeder-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5160
432 | GIS feeder-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5161
433 | GIS feeder-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5162
434 | GIS feeder-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5163
435 | GIS feeder-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5164
436 | GIS feeder-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5165
437 | GIS feeder-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5166
438 | GIS feeder-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5167
439 | GIS feeder-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5168
440 | GIS feeder-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5169
441 | GIS\Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 212
442 | GIS\Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 213
443 | GIS\Salt lake fdr-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 214
444 | GIS\Salt lake fdr-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 215
445 | GIS\Salt lake fdr-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 216
446 | GIS\Salt lake fdr-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 217
447 | GIS\Salt lake fdr-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 218
448 | GIS\Salt lake fdr-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 219
449 | GIS\Salt lake fdr-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 220
450 | GIS\Salt lake fdr-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 221
451 | GIS\Salt lake fdr-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 222
452 | GIS\Salt lake fdr-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 223
453 | GIS\Salt lake fdr-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
454 | GIS\Salt lake fdr-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13040
455 | GIS\Salt lake fdr-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13041
456 | GIS\Salt lake fdr-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
457 | GIS\Salt lake fdr-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
458 | GIS\Salt lake fdr-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5170
459 | GIS\Salt lake fdr-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5171
460 | GIS\Salt lake fdr-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5172
461 | GIS\Salt lake fdr-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5173
462 | GIS\Salt lake fdr-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5174
463 | GIS\Salt lake fdr-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5175
464 | GIS\Salt lake fdr-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5176
465 | GIS\Salt lake fdr-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5177
466 | GIS\Salt lake fdr-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5178
467 | GIS\Salt lake fdr-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5179
468 | GIS\Salt lake fdr-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5180
469 | GIS\Salt lake fdr-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5181
470 | GIS\Salt lake fdr-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5182
471 | GIS\Salt lake fdr-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5183
472 | GIS\Salt lake fdr-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5184
473 | GIS\Salt lake fdr-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5185
474 | GIS\Salt lake fdr-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5186
475 | GIS\Salt lake fdr-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5187
476 | GIS\Salt lake fdr-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5188
477 | M1\M21 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 224
478 | M1\M21 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 225
479 | M1\M21 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 226
480 | M1\M21 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 227
481 | M1\M21 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 228
482 | M1\M21 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 229
483 | M1\M21 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 230
484 | M1\M21 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 231
485 | M1\M21 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 232
486 | M1\M21 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 233
487 | M1\M21 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 234
488 | M1\M21 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 235
489 | M1\M21 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 236
490 | M1\M21 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 237
491 | M1\M21 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
492 | M1\M21 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
493 | M1\M21 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
494 | M1\M21 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13043
495 | M1\M21 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13044
496 | M1\M21 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5189
497 | M1\M21 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5190
498 | M1\M21 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5191
499 | M1\M21 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5192
500 | M1\M21 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5193
501 | M1\M21 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5194
502 | M1\M21 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5195
503 | M1\M21 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5196
504 | M1\M21 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5197
505 | M1\M21 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5198
506 | M1\M21 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5199
507 | M1\M21 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5200
508 | M1\M21 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5201
509 | M1\M21 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5202
510 | M1\M21 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5203
511 | M1\M21 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5204
512 | M1\M21 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5205
513 | R Switching SS | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 238
514 | R Switching SS | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 239
515 | R Switching SS | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 240
516 | R Switching SS | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 241
517 | R Switching SS | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 242
518 | R Switching SS | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 243
519 | R Switching SS | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 244
520 | R Switching SS | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 245
521 | R Switching SS | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 246
522 | R Switching SS | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 247
523 | R Switching SS | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 248
524 | R Switching SS | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 249
525 | R Switching SS | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 250
526 | R Switching SS | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 251
527 | R Switching SS | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
528 | R Switching SS | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
529 | R Switching SS | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
530 | R Switching SS | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
531 | R Switching SS | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
532 | R Switching SS | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5206
533 | R Switching SS | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5207
534 | R Switching SS | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5208
535 | R Switching SS | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5209
536 | R Switching SS | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5210
537 | R Switching SS | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5211
538 | R Switching SS | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5212
539 | R Switching SS | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5213
540 | R Switching SS | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5214
541 | R Switching SS | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5215
542 | R Switching SS | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5216
543 | R Switching SS | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5217
544 | R Switching SS | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5218
545 | R Switching SS | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5219
546 | R Switching SS | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5220
547 | R Switching SS | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5221
548 | R Switching SS | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5222
549 | Tr No-4 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 252
550 | Tr No-4 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 253
551 | Tr No-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 254
552 | Tr No-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 255
553 | Tr No-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 256
554 | Tr No-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 257
555 | Tr No-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 258
556 | Tr No-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 259
557 | Tr No-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 260
558 | Tr No-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 261
559 | Tr No-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 262
560 | Tr No-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 263
561 | Tr No-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 264
562 | Tr No-4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
563 | Tr No-4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
564 | Tr No-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
565 | Tr No-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13049
566 | Tr No-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13050
567 | Tr No-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5223
568 | Tr No-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5224
569 | Tr No-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5225
570 | Tr No-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5226
571 | Tr No-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5227
572 | Tr No-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5228
573 | Tr No-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5229
574 | Tr No-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5230
575 | Tr No-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5231
576 | Tr No-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5232
577 | Tr No-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5233
578 | Tr No-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5234
579 | Tr No-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5235
580 | Tr No-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5236
581 | Tr No-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5237
582 | Tr No-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5238
583 | Tr No-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5239
584 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 265
585 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 266
586 | Bus Coupler-3 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 267
587 | Bus Coupler-3 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 268
588 | Bus Coupler-3 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 269
589 | Bus Coupler-3 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 270
590 | Bus Coupler-3 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 271
591 | Bus Coupler-3 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 272 |  |  |  | AC CMR to be used
592 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 273
593 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 274
594 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10013
595 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10013
596 | BSNL (p&T) | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 275
597 | BSNL (p&T) | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 276
598 | BSNL (p&T) | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 277
599 | BSNL (p&T) | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 278
600 | BSNL (p&T) | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 279
601 | BSNL (p&T) | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 280
602 | BSNL (p&T) | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 281
603 | BSNL (p&T) | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 282
604 | BSNL (p&T) | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 283
605 | BSNL (p&T) | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 284
606 | BSNL (p&T) | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 285
607 | BSNL (p&T) | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 286
608 | BSNL (p&T) | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 287
609 | BSNL (p&T) | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 288
610 | BSNL (p&T) | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
611 | BSNL (p&T) | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
612 | BSNL (p&T) | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
613 | BSNL (p&T) | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
614 | BSNL (p&T) | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
615 | BSNL (p&T) | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5240
616 | BSNL (p&T) | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5241
617 | BSNL (p&T) | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5242
618 | BSNL (p&T) | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5243
619 | BSNL (p&T) | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5244
620 | BSNL (p&T) | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5245
621 | BSNL (p&T) | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5246
622 | BSNL (p&T) | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5247
623 | BSNL (p&T) | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5248
624 | BSNL (p&T) | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5249
625 | BSNL (p&T) | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5250
626 | BSNL (p&T) | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5251
627 | BSNL (p&T) | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5252
628 | BSNL (p&T) | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5253
629 | BSNL (p&T) | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5254
630 | BSNL (p&T) | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5255
631 | BSNL (p&T) | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5256
632 | D Switching SS | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 289
633 | D Switching SS | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 290
634 | D Switching SS | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 291
635 | D Switching SS | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 292
636 | D Switching SS | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 293
637 | D Switching SS | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 294
638 | D Switching SS | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 295
639 | D Switching SS | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 296
640 | D Switching SS | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 297
641 | D Switching SS | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 298
642 | D Switching SS | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 299
643 | D Switching SS | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 300
644 | D Switching SS | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 301
645 | D Switching SS | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 302
646 | D Switching SS | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
647 | D Switching SS | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
648 | D Switching SS | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
649 | D Switching SS | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
650 | D Switching SS | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
651 | D Switching SS | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5257
652 | D Switching SS | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5258
653 | D Switching SS | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5259
654 | D Switching SS | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5260
655 | D Switching SS | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5261
656 | D Switching SS | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5262
657 | D Switching SS | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5263
658 | D Switching SS | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5264
659 | D Switching SS | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5265
660 | D Switching SS | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5266
661 | D Switching SS | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5267
662 | D Switching SS | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5268
663 | D Switching SS | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5269
664 | D Switching SS | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5270
665 | D Switching SS | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5271
666 | D Switching SS | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5272
667 | D Switching SS | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5273
668 | Tr No-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 303
669 | Tr No-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 304
670 | Tr No-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 305
671 | Tr No-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 306
672 | Tr No-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 307
673 | Tr No-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 308
674 | Tr No-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 309
675 | Tr No-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 310
676 | Tr No-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 311
677 | Tr No-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 312
678 | Tr No-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 313
679 | Tr No-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 314
680 | Tr No-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 315
681 | Tr No-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
682 | Tr No-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
683 | Tr No-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
684 | Tr No-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13058
685 | Tr No-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13059
686 | Tr No-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5274
687 | Tr No-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5275
688 | Tr No-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5276
689 | Tr No-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5277
690 | Tr No-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5278
691 | Tr No-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5279
692 | Tr No-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5280
693 | Tr No-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5281
694 | Tr No-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5282
695 | Tr No-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5283
696 | Tr No-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5284
697 | Tr No-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5285
698 | Tr No-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5286
699 | Tr No-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5287
700 | Tr No-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5288
701 | Tr No-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5289
702 | Tr No-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5290
703 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 316
704 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 317
705 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 318
706 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 319
707 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 320
708 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 321
709 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 322
710 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 323 |  |  |  | AC CMR to be used
711 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 324
712 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 325
713 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10017
714 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10017
715 | 4 - Pole | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 326
716 | 4 - Pole | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 327
717 | 4 - Pole | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 328
718 | 4 - Pole | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 329
719 | 4 - Pole | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 330
720 | 4 - Pole | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 331
721 | 4 - Pole | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 332
722 | 4 - Pole | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 333
723 | 4 - Pole | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 334
724 | 4 - Pole | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 335
725 | 4 - Pole | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 336
726 | 4 - Pole | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 337
727 | 4 - Pole | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 338
728 | 4 - Pole | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 339
729 | 4 - Pole | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
730 | 4 - Pole | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
731 | 4 - Pole | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
732 | 4 - Pole | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
733 | 4 - Pole | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
734 | 4 - Pole | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5291
735 | 4 - Pole | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5292
736 | 4 - Pole | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5293
737 | 4 - Pole | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5294
738 | 4 - Pole | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5295
739 | 4 - Pole | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5296
740 | 4 - Pole | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5297
741 | 4 - Pole | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5298
742 | 4 - Pole | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5299
743 | 4 - Pole | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5300
744 | 4 - Pole | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5301
745 | 4 - Pole | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5302
746 | 4 - Pole | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5303
747 | 4 - Pole | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5304
748 | 4 - Pole | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5305
749 | 4 - Pole | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5306
750 | 4 - Pole | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5307
751 | CMDA | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 340
752 | CMDA | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 341
753 | CMDA | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 342
754 | CMDA | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 343
755 | CMDA | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 344
756 | CMDA | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 345
757 | CMDA | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 346
758 | CMDA | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 347
759 | CMDA | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 348
760 | CMDA | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 349
761 | CMDA | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 350
762 | CMDA | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 351
763 | CMDA | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 352
764 | CMDA | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 353
765 | CMDA | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
766 | CMDA | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
767 | CMDA | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
768 | CMDA | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
769 | CMDA | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
770 | CMDA | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5308
771 | CMDA | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5309
772 | CMDA | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5310
773 | CMDA | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5311
774 | CMDA | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5312
775 | CMDA | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5313
776 | CMDA | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5314
777 | CMDA | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5315
778 | CMDA | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5316
779 | CMDA | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5317
780 | CMDA | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5318
781 | CMDA | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5319
782 | CMDA | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5320
783 | CMDA | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5321
784 | CMDA | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5322
785 | CMDA | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5323
786 | CMDA | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5324
787 | C Switching | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 354
788 | C Switching | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 355
789 | C Switching | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 356
790 | C Switching | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 357
791 | C Switching | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 358
792 | C Switching | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 359
793 | C Switching | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 360
794 | C Switching | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 361
795 | C Switching | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 362
796 | C Switching | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 363
797 | C Switching | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 364
798 | C Switching | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 365
799 | C Switching | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 366
800 | C Switching | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 367
801 | C Switching | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
802 | C Switching | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
803 | C Switching | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
804 | C Switching | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
805 | C Switching | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
806 | C Switching | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5325
807 | C Switching | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5326
808 | C Switching | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5327
809 | C Switching | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5328
810 | C Switching | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5329
811 | C Switching | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5330
812 | C Switching | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5331
813 | C Switching | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5332
814 | C Switching | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5333
815 | C Switching | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5334
816 | C Switching | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5335
817 | C Switching | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5336
818 | C Switching | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5337
819 | C Switching | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5338
820 | C Switching | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5339
821 | C Switching | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5340
822 | C Switching | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5341
823 | Tr No - 2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 368
824 | Tr No - 2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 369
825 | Tr No - 2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 370
826 | Tr No - 2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 371
827 | Tr No - 2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 372
828 | Tr No - 2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 373
829 | Tr No - 2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 374
830 | Tr No - 2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 375
831 | Tr No - 2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 376
832 | Tr No - 2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 377
833 | Tr No - 2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 378
834 | Tr No - 2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 379
835 | Tr No - 2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 380
836 | Tr No - 2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
837 | Tr No - 2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
838 | Tr No - 2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
839 | Tr No - 2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13070
840 | Tr No - 2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13071
841 | Tr No - 2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5342
842 | Tr No - 2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5343
843 | Tr No - 2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5344
844 | Tr No - 2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5345
845 | Tr No - 2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5346
846 | Tr No - 2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5347
847 | Tr No - 2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5348
848 | Tr No - 2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5349
849 | Tr No - 2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5350
850 | Tr No - 2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5351
851 | Tr No - 2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5352
852 | Tr No - 2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5353
853 | Tr No - 2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5354
854 | Tr No - 2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5355
855 | Tr No - 2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5356
856 | Tr No - 2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5357
857 | Tr No - 2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5358
858 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 381
859 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 382
860 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 383
861 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 384
862 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 385
863 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 386
864 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 387
865 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 388 |  |  |  | AC CMR to be used
866 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 389
867 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 390
868 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10022
869 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10022
870 | M1-M2 inter connector | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 391
871 | M1-M2 inter connector | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 392
872 | M1-M2 inter connector | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 393
873 | M1-M2 inter connector | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 394
874 | M1-M2 inter connector | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 395
875 | M1-M2 inter connector | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 396
876 | M1-M2 inter connector | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 397
877 | M1-M2 inter connector | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 398
878 | M1-M2 inter connector | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 399
879 | M1-M2 inter connector | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 400
880 | M1-M2 inter connector | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 401
881 | M1-M2 inter connector | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 402
882 | M1-M2 inter connector | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 403
883 | M1-M2 inter connector | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
884 | M1-M2 inter connector | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
885 | M1-M2 inter connector | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
886 | M1-M2 inter connector | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13073
887 | M1-M2 inter connector | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13074
888 | M1-M2 inter connector | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5359
889 | M1-M2 inter connector | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5360
890 | M1-M2 inter connector | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5361
891 | M1-M2 inter connector | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5362
892 | M1-M2 inter connector | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5363
893 | M1-M2 inter connector | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5364
894 | M1-M2 inter connector | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5365
895 | M1-M2 inter connector | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5366
896 | M1-M2 inter connector | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5367
897 | M1-M2 inter connector | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5368
898 | M1-M2 inter connector | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5369
899 | M1-M2 inter connector | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5370
900 | M1-M2 inter connector | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5371
901 | M1-M2 inter connector | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5372
902 | M1-M2 inter connector | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5373
903 | M1-M2 inter connector | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5374
904 | M1-M2 inter connector | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5375
905 | A switching | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 404
906 | A switching | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 405
907 | A switching | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 406
908 | A switching | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 407
909 | A switching | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 408
910 | A switching | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 409
911 | A switching | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 410
912 | A switching | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 411
913 | A switching | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 412
914 | A switching | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 413
915 | A switching | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 414
916 | A switching | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 415
917 | A switching | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 416
918 | A switching | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 417
919 | A switching | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
920 | A switching | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
921 | A switching | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
922 | A switching | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13076
923 | A switching | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13077
924 | A switching | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5376
925 | A switching | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5377
926 | A switching | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5378
927 | A switching | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5379
928 | A switching | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5380
929 | A switching | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5381
930 | A switching | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5382
931 | A switching | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5383
932 | A switching | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5384
933 | A switching | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5385
934 | A switching | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5386
935 | A switching | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5387
936 | A switching | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5388
937 | A switching | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5389
938 | A switching | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5390
939 | A switching | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5391
940 | A switching | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5392
941 | M1\M11 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 418
942 | M1\M11 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 419
943 | M1\M11 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 420
944 | M1\M11 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 421
945 | M1\M11 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 422
946 | M1\M11 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 423
947 | M1\M11 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 424
948 | M1\M11 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 425
949 | M1\M11 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 426
950 | M1\M11 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 427
951 | M1\M11 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 428
952 | M1\M11 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 429
953 | M1\M11 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 430
954 | M1\M11 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 431
955 | M1\M11 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10025
956 | M1\M11 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10025
957 | M1\M11 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
958 | M1\M11 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13079
959 | M1\M11 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13080
960 | M1\M11 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5393
961 | M1\M11 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5394
962 | M1\M11 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5395
963 | M1\M11 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5396
964 | M1\M11 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5397
965 | M1\M11 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5398
966 | M1\M11 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5399
967 | M1\M11 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5400
968 | M1\M11 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5401
969 | M1\M11 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5402
970 | M1\M11 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5403
971 | M1\M11 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5404
972 | M1\M11 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5405
973 | M1\M11 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5406
974 | M1\M11 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5407
975 | M1\M11 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5408
976 | M1\M11 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5409
977 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 432
978 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 433
979 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 434
980 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 435
981 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 436
982 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 437
983 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 438
984 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 439
985 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 440
986 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 441
987 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 442
988 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 443
989 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 444
990 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
991 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
992 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
993 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13082
994 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13083
995 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5410
996 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5411
997 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5412
998 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5413
999 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5414
1000 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5415
1001 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5416
1002 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5417
1003 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5418
1004 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5419
1005 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5420
1006 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5421
1007 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5422
1008 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5423
1009 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5424
1010 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5425
1011 | Inter connector Tr No.1 & Tr No.5 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5426
1012 | Tr No-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 445
1013 | Tr No-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 446
1014 | Tr No-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 447
1015 | Tr No-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 448
1016 | Tr No-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 449
1017 | Tr No-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 450
1018 | Tr No-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 451
1019 | Tr No-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 452
1020 | Tr No-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 453
1021 | Tr No-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 454
1022 | Tr No-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 455
1023 | Tr No-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 456
1024 | Tr No-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 457
1025 | Tr No-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10027
1026 | Tr No-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10027
1027 | Tr No-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1028 | Tr No-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1029 | Tr No-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13086
1030 | Tr No-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5427
1031 | Tr No-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5428
1032 | Tr No-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5429
1033 | Tr No-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5430
1034 | Tr No-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5431
1035 | Tr No-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5432
1036 | Tr No-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5433
1037 | Tr No-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5434
1038 | Tr No-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5435
1039 | Tr No-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5436
1040 | Tr No-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5437
1041 | Tr No-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5438
1042 | Tr No-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5439
1043 | Tr No-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5440
1044 | Tr No-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5441
1045 | Tr No-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5442
1046 | Tr No-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5443
1047 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 458
1048 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 459
1049 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 460
1050 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 461
1051 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 462
1052 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 463
1053 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 464
1054 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 465
1055 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 466
1056 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 467
1057 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 468
1058 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 469
1059 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 470
1060 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 471
1061 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10028
1062 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10028
1063 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1064 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1065 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13089
1066 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5444
1067 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5445
1068 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5446
1069 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5447
1070 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5448
1071 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5449
1072 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5450
1073 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5451
1074 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5452
1075 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5453
1076 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5454
1077 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5455
1078 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5456
1079 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5457
1080 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5458
1081 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5459
1082 | Tr5 & Tr1 Inter connector | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5460
1083 | Bengal Ambuja | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 472
1084 | Bengal Ambuja | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 473
1085 | Bengal Ambuja | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 474
1086 | Bengal Ambuja | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 475
1087 | Bengal Ambuja | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 476
1088 | Bengal Ambuja | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 477
1089 | Bengal Ambuja | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 478
1090 | Bengal Ambuja | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 479
1091 | Bengal Ambuja | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 480
1092 | Bengal Ambuja | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 481
1093 | Bengal Ambuja | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 482
1094 | Bengal Ambuja | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 483
1095 | Bengal Ambuja | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 484
1096 | Bengal Ambuja | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 485
1097 | Bengal Ambuja | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10029
1098 | Bengal Ambuja | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10029
1099 | Bengal Ambuja | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1100 | Bengal Ambuja | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1101 | Bengal Ambuja | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13092
1102 | Bengal Ambuja | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5461
1103 | Bengal Ambuja | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5462
1104 | Bengal Ambuja | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5463
1105 | Bengal Ambuja | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5464
1106 | Bengal Ambuja | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5465
1107 | Bengal Ambuja | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5466
1108 | Bengal Ambuja | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5467
1109 | Bengal Ambuja | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5468
1110 | Bengal Ambuja | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5469
1111 | Bengal Ambuja | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5470
1112 | Bengal Ambuja | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5471
1113 | Bengal Ambuja | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5472
1114 | Bengal Ambuja | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5473
1115 | Bengal Ambuja | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5474
1116 | Bengal Ambuja | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5475
1117 | Bengal Ambuja | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5476
1118 | Bengal Ambuja | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5477
1119 | B Switching | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 486
1120 | B Switching | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 487
1121 | B Switching | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 488
1122 | B Switching | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 489
1123 | B Switching | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 490
1124 | B Switching | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 491
1125 | B Switching | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 492
1126 | B Switching | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 493
1127 | B Switching | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 494
1128 | B Switching | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 495
1129 | B Switching | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 496
1130 | B Switching | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 497
1131 | B Switching | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 498
1132 | B Switching | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 499
1133 | B Switching | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10030
1134 | B Switching | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10030
1135 | B Switching | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13093
1136 | B Switching | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13094
1137 | B Switching | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13095
1138 | B Switching | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5478
1139 | B Switching | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5479
1140 | B Switching | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5480
1141 | B Switching | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5481
1142 | B Switching | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5482
1143 | B Switching | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5483
1144 | B Switching | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5484
1145 | B Switching | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5485
1146 | B Switching | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5486
1147 | B Switching | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5487
1148 | B Switching | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5488
1149 | B Switching | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5489
1150 | B Switching | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5490
1151 | B Switching | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5491
1152 | B Switching | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5492
1153 | B Switching | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5493
1154 | B Switching | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5494
1155 | TRF -1 (I\C Trs) | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 500
1156 | TRF -1 (I\C Trs) | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 501
1157 | TRF -1 (I\C Trs) | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 502
1158 | TRF -1 (I\C Trs) | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 503
1159 | TRF -1 (I\C Trs) | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 504
1160 | TRF -1 (I\C Trs) | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 505
1161 | TRF -1 (I\C Trs) | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 506
1162 | TRF -1 (I\C Trs) | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 507
1163 | TRF -1 (I\C Trs) | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 508
1164 | TRF -1 (I\C Trs) | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 509
1165 | TRF -1 (I\C Trs) | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 510
1166 | TRF -1 (I\C Trs) | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 511
1167 | TRF -1 (I\C Trs) | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 512
1168 | TRF -1 (I\C Trs) | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10031
1169 | TRF -1 (I\C Trs) | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10031
1170 | TRF -1 (I\C Trs) | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13096
1171 | TRF -1 (I\C Trs) | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13097
1172 | TRF -1 (I\C Trs) | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13098
1173 | TRF -1 (I\C Trs) | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5495
1174 | TRF -1 (I\C Trs) | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5496
1175 | TRF -1 (I\C Trs) | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5497
1176 | TRF -1 (I\C Trs) | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5498
1177 | TRF -1 (I\C Trs) | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5499
1178 | TRF -1 (I\C Trs) | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5500
1179 | TRF -1 (I\C Trs) | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5501
1180 | TRF -1 (I\C Trs) | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5502
1181 | TRF -1 (I\C Trs) | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5503
1182 | TRF -1 (I\C Trs) | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5504
1183 | TRF -1 (I\C Trs) | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5505
1184 | TRF -1 (I\C Trs) | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5506
1185 | TRF -1 (I\C Trs) | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5507
1186 | TRF -1 (I\C Trs) | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5508
1187 | TRF -1 (I\C Trs) | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5509
1188 | TRF -1 (I\C Trs) | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5510
1189 | TRF -1 (I\C Trs) | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5511
1190 | TR-5 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 513
1191 | TR-5 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 514
1192 | TR-5 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 515
1193 | TR-5 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 516
1194 | TR-5 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 517
1195 | TR-5 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 518
1196 | TR-5 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 519
1197 | TR-5 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 520
1198 | TR-5 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 521
1199 | TR-5 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 522
1200 | TR-5 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 523
1201 | TR-5 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 524
1202 | TR-5 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 525
1203 | TR-5 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10032
1204 | TR-5 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10032
1205 | TR-5 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13099
1206 | TR-5 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13100
1207 | TR-5 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13101
1208 | TR-5 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5512
1209 | TR-5 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5513
1210 | TR-5 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5514
1211 | TR-5 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5515
1212 | TR-5 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5516
1213 | TR-5 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5517
1214 | TR-5 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5518
1215 | TR-5 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5519
1216 | TR-5 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5520
1217 | TR-5 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5521
1218 | TR-5 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5522
1219 | TR-5 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5523
1220 | TR-5 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5524
1221 | TR-5 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5525
1222 | TR-5 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5526
1223 | TR-5 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5527
1224 | TR-5 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5528
1225 | ACDB 1 | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5529
1226 | ACDB 1 | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5530
1227 | ACDB 1 | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5531
1228 | ACDB 1 | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5532
1229 | ACDB 1 | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5533
1230 | ACDB 1 | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5534
1231 | ACDB 1 | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5535
1232 | ACDB 2 | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5536
1233 | ACDB 2 | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5537
1234 | ACDB 2 | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5538
1235 | ACDB 2 | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5539
1236 | ACDB 2 | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5540
1237 | ACDB 2 | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5541
1238 | ACDB 2 | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5542