## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | DUMMY CB | 3000
23 | Sub-Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | DUMMY CB | 10000
24 | Sub-Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer-3 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer-3 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | Transformer-4 | 33kV | Transformer | Circuit breaker Close | SPI |  |  | Soft | IED1 | 112
209 | Transformer-4 | 33kV | Transformer | Circuit breaker Open | SPI |  |  | Soft | IED1 | 113
210 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 114
211 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 115
212 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 116
213 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 117
214 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 118
215 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 119
216 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 120
217 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 121
218 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 122
219 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 123
220 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 124
221 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 125
222 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 126
223 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 127
224 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 128
225 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 129
226 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 130
227 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 131
228 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 132
229 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 133
230 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 134
231 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 135
232 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
233 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
234 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
235 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
236 | Transformer-4 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
237 | Transformer-4 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
238 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5068
239 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5069
240 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5070
241 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5071
242 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5072
243 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5073
244 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5074
245 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5075
246 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5076
247 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5077
248 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5078
249 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5079
250 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5080
251 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5081
252 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5082
253 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
254 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
255 | Transformer-4 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 136
256 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 137
257 | Transformer-4 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 138 |  |  |  | AC CMR to be used
258 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 139
259 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 140
260 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 141
261 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 142
262 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 143
263 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
264 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
265 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5085
266 | Transformer-4 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5086
267 | Transformer-4 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5087
268 | GIS Fdr-1 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 144
269 | GIS Fdr-1 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 145
270 | GIS Fdr-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 146
271 | GIS Fdr-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 147
272 | GIS Fdr-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 148
273 | GIS Fdr-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 149
274 | GIS Fdr-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 150
275 | GIS Fdr-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 151
276 | GIS Fdr-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 152
277 | GIS Fdr-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 153
278 | GIS Fdr-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 154
279 | GIS Fdr-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 155
280 | GIS Fdr-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13024
281 | GIS Fdr-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13025
282 | GIS Fdr-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13026
283 | GIS Fdr-1 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10005
284 | GIS Fdr-1 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10005
285 | GIS Fdr-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5088
286 | GIS Fdr-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5089
287 | GIS Fdr-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5090
288 | GIS Fdr-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5091
289 | GIS Fdr-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5092
290 | GIS Fdr-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5093
291 | GIS Fdr-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5094
292 | GIS Fdr-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5095
293 | GIS Fdr-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5096
294 | GIS Fdr-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5097
295 | GIS Fdr-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5098
296 | GIS Fdr-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5099
297 | GIS Fdr-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5100
298 | GIS Fdr-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5101
299 | GIS Fdr-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5102
300 | GIS Fdr-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5103
301 | GIS Fdr-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5104
302 | GIS Fdr-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5105
303 | GIS Fdr-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5106
304 | Bagjola | 33kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 156
305 | Bagjola | 33kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 157
306 | Bagjola | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 158
307 | Bagjola | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 159
308 | Bagjola | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 160
309 | Bagjola | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 161
310 | Bagjola | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 162
311 | Bagjola | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 163
312 | Bagjola | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 164
313 | Bagjola | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 165
314 | Bagjola | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 166
315 | Bagjola | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 167
316 | Bagjola | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13027
317 | Bagjola | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13028
318 | Bagjola | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13029
319 | Bagjola | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
320 | Bagjola | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
321 | Bagjola | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5107
322 | Bagjola | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5108
323 | Bagjola | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5109
324 | Bagjola | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5110
325 | Bagjola | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5111
326 | Bagjola | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5112
327 | Bagjola | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5113
328 | Bagjola | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5114
329 | Bagjola | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5115
330 | Bagjola | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5116
331 | Bagjola | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5117
332 | Bagjola | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5118
333 | Bagjola | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5119
334 | Bagjola | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5120
335 | Bagjola | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5121
336 | Bagjola | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5122
337 | Bagjola | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5123
338 | Bagjola | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5124
339 | Bagjola | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5125
340 | HSBC fdr | 33kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 168
341 | HSBC fdr | 33kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 169
342 | HSBC fdr | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 170
343 | HSBC fdr | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 171
344 | HSBC fdr | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 172
345 | HSBC fdr | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 173
346 | HSBC fdr | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 174
347 | HSBC fdr | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 175
348 | HSBC fdr | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 176
349 | HSBC fdr | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 177
350 | HSBC fdr | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 178
351 | HSBC fdr | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 179
352 | HSBC fdr | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
353 | HSBC fdr | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
354 | HSBC fdr | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13032
355 | HSBC fdr | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
356 | HSBC fdr | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
357 | HSBC fdr | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5126
358 | HSBC fdr | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5127
359 | HSBC fdr | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5128
360 | HSBC fdr | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5129
361 | HSBC fdr | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5130
362 | HSBC fdr | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5131
363 | HSBC fdr | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5132
364 | HSBC fdr | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5133
365 | HSBC fdr | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5134
366 | HSBC fdr | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5135
367 | HSBC fdr | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5136
368 | HSBC fdr | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5137
369 | HSBC fdr | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5138
370 | HSBC fdr | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5139
371 | HSBC fdr | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5140
372 | HSBC fdr | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5141
373 | HSBC fdr | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5142
374 | HSBC fdr | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5143
375 | HSBC fdr | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5144
376 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 180
377 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 181
378 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 182
379 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 183
380 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 184
381 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 185
382 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 186
383 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 187
384 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 188
385 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 189
386 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 190
387 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 191
388 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
389 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13034
390 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13035
391 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
392 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
393 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5145
394 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5146
395 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5147
396 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5148
397 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5149
398 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5150
399 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5151
400 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5152
401 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5153
402 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5154
403 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5155
404 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5156
405 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5157
406 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5158
407 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5159
408 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5160
409 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5161
410 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5162
411 | Salt lake fdr-1 & Bantala fdr-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5163
412 | GIS fdr-2 | 33kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 192
413 | GIS fdr-2 | 33kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 193
414 | GIS fdr-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 194
415 | GIS fdr-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 195
416 | GIS fdr-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 196
417 | GIS fdr-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 197
418 | GIS fdr-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 198
419 | GIS fdr-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 199
420 | GIS fdr-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 200
421 | GIS fdr-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 201
422 | GIS fdr-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 202
423 | GIS fdr-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 203
424 | GIS fdr-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
425 | GIS fdr-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
426 | GIS fdr-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13038
427 | GIS fdr-2 | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
428 | GIS fdr-2 | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
429 | GIS fdr-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5164
430 | GIS fdr-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5165
431 | GIS fdr-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5166
432 | GIS fdr-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5167
433 | GIS fdr-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5168
434 | GIS fdr-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5169
435 | GIS fdr-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5170
436 | GIS fdr-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5171
437 | GIS fdr-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5172
438 | GIS fdr-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5173
439 | GIS fdr-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5174
440 | GIS fdr-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5175
441 | GIS fdr-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5176
442 | GIS fdr-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5177
443 | GIS fdr-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5178
444 | GIS fdr-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5179
445 | GIS fdr-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5180
446 | GIS fdr-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5181
447 | GIS fdr-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5182
448 | H Feeder | 33kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 204
449 | H Feeder | 33kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 205
450 | H Feeder | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 206
451 | H Feeder | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 207
452 | H Feeder | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 208
453 | H Feeder | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 209
454 | H Feeder | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 210
455 | H Feeder | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 211
456 | H Feeder | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 212
457 | H Feeder | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 213
458 | H Feeder | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 214
459 | H Feeder | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 215
460 | H Feeder | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
461 | H Feeder | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13040
462 | H Feeder | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13041
463 | H Feeder | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
464 | H Feeder | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
465 | H Feeder | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5183
466 | H Feeder | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5184
467 | H Feeder | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5185
468 | H Feeder | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5186
469 | H Feeder | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5187
470 | H Feeder | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5188
471 | H Feeder | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5189
472 | H Feeder | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5190
473 | H Feeder | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5191
474 | H Feeder | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5192
475 | H Feeder | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5193
476 | H Feeder | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5194
477 | H Feeder | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5195
478 | H Feeder | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5196
479 | H Feeder | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5197
480 | H Feeder | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5198
481 | H Feeder | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5199
482 | H Feeder | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5200
483 | H Feeder | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5201
484 | TR-3 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 216
485 | TR-3 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 217
486 | TR-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 218
487 | TR-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 219
488 | TR-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 220
489 | TR-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 221
490 | TR-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 222
491 | TR-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 223
492 | TR-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 224
493 | TR-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 225
494 | TR-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 226
495 | TR-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 227
496 | TR-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 228
497 | TR-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
498 | TR-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
499 | TR-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
500 | TR-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13043
501 | TR-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13044
502 | TR-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5202
503 | TR-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5203
504 | TR-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5204
505 | TR-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5205
506 | TR-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5206
507 | TR-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5207
508 | TR-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5208
509 | TR-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5209
510 | TR-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5210
511 | TR-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5211
512 | TR-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5212
513 | TR-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5213
514 | TR-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5214
515 | TR-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5215
516 | TR-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5216
517 | TR-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5217
518 | TR-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5218
519 | D-13\Purta Bhavan | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 229
520 | D-13\Purta Bhavan | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 230
521 | D-13\Purta Bhavan | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 231
522 | D-13\Purta Bhavan | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 232
523 | D-13\Purta Bhavan | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 233
524 | D-13\Purta Bhavan | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 234
525 | D-13\Purta Bhavan | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 235
526 | D-13\Purta Bhavan | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 236
527 | D-13\Purta Bhavan | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 237
528 | D-13\Purta Bhavan | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 238
529 | D-13\Purta Bhavan | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 239
530 | D-13\Purta Bhavan | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 240
531 | D-13\Purta Bhavan | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 241
532 | D-13\Purta Bhavan | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 242
533 | D-13\Purta Bhavan | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
534 | D-13\Purta Bhavan | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
535 | D-13\Purta Bhavan | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
536 | D-13\Purta Bhavan | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
537 | D-13\Purta Bhavan | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13047
538 | D-13\Purta Bhavan | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5219
539 | D-13\Purta Bhavan | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5220
540 | D-13\Purta Bhavan | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5221
541 | D-13\Purta Bhavan | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5222
542 | D-13\Purta Bhavan | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5223
543 | D-13\Purta Bhavan | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5224
544 | D-13\Purta Bhavan | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5225
545 | D-13\Purta Bhavan | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5226
546 | D-13\Purta Bhavan | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5227
547 | D-13\Purta Bhavan | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5228
548 | D-13\Purta Bhavan | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5229
549 | D-13\Purta Bhavan | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5230
550 | D-13\Purta Bhavan | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5231
551 | D-13\Purta Bhavan | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5232
552 | D-13\Purta Bhavan | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5233
553 | D-13\Purta Bhavan | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5234
554 | D-13\Purta Bhavan | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5235
555 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 243
556 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 244
557 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 245
558 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 246
559 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 247
560 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 248
561 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 249
562 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 250
563 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 251
564 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 252
565 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 253
566 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 254
567 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 255
568 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 256
569 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
570 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
571 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
572 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
573 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13050
574 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5236
575 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5237
576 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5238
577 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5239
578 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5240
579 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5241
580 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5242
581 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5243
582 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5244
583 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5245
584 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5246
585 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5247
586 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5248
587 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5249
588 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5250
589 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5251
590 | M1 Bidyut Bhavan via M4 M2 int conn | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5252
591 | M-11\M-31 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 257
592 | M-11\M-31 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 258
593 | M-11\M-31 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 259
594 | M-11\M-31 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 260
595 | M-11\M-31 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 261
596 | M-11\M-31 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 262
597 | M-11\M-31 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 263
598 | M-11\M-31 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 264
599 | M-11\M-31 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 265
600 | M-11\M-31 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 266
601 | M-11\M-31 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 267
602 | M-11\M-31 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 268
603 | M-11\M-31 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 269
604 | M-11\M-31 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 270
605 | M-11\M-31 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
606 | M-11\M-31 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
607 | M-11\M-31 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
608 | M-11\M-31 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13052
609 | M-11\M-31 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13053
610 | M-11\M-31 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5253
611 | M-11\M-31 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5254
612 | M-11\M-31 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5255
613 | M-11\M-31 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5256
614 | M-11\M-31 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5257
615 | M-11\M-31 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5258
616 | M-11\M-31 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5259
617 | M-11\M-31 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5260
618 | M-11\M-31 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5261
619 | M-11\M-31 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5262
620 | M-11\M-31 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5263
621 | M-11\M-31 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5264
622 | M-11\M-31 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5265
623 | M-11\M-31 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5266
624 | M-11\M-31 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5267
625 | M-11\M-31 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5268
626 | M-11\M-31 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5269
627 | Haldia Petrochemical | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 271
628 | Haldia Petrochemical | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 272
629 | Haldia Petrochemical | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 273
630 | Haldia Petrochemical | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 274
631 | Haldia Petrochemical | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 275
632 | Haldia Petrochemical | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 276
633 | Haldia Petrochemical | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 277
634 | Haldia Petrochemical | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 278
635 | Haldia Petrochemical | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 279
636 | Haldia Petrochemical | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 280
637 | Haldia Petrochemical | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 281
638 | Haldia Petrochemical | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 282
639 | Haldia Petrochemical | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 283
640 | Haldia Petrochemical | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 284
641 | Haldia Petrochemical | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
642 | Haldia Petrochemical | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
643 | Haldia Petrochemical | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
644 | Haldia Petrochemical | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
645 | Haldia Petrochemical | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
646 | Haldia Petrochemical | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5270
647 | Haldia Petrochemical | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5271
648 | Haldia Petrochemical | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5272
649 | Haldia Petrochemical | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5273
650 | Haldia Petrochemical | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5274
651 | Haldia Petrochemical | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5275
652 | Haldia Petrochemical | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5276
653 | Haldia Petrochemical | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5277
654 | Haldia Petrochemical | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5278
655 | Haldia Petrochemical | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5279
656 | Haldia Petrochemical | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5280
657 | Haldia Petrochemical | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5281
658 | Haldia Petrochemical | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5282
659 | Haldia Petrochemical | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5283
660 | Haldia Petrochemical | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5284
661 | Haldia Petrochemical | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5285
662 | Haldia Petrochemical | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5286
663 | F Switching | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 285
664 | F Switching | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 286
665 | F Switching | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 287
666 | F Switching | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 288
667 | F Switching | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 289
668 | F Switching | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 290
669 | F Switching | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 291
670 | F Switching | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 292
671 | F Switching | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 293
672 | F Switching | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 294
673 | F Switching | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 295
674 | F Switching | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 296
675 | F Switching | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 297
676 | F Switching | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 298
677 | F Switching | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
678 | F Switching | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
679 | F Switching | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
680 | F Switching | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
681 | F Switching | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
682 | F Switching | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5287
683 | F Switching | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5288
684 | F Switching | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5289
685 | F Switching | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5290
686 | F Switching | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5291
687 | F Switching | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5292
688 | F Switching | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5293
689 | F Switching | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5294
690 | F Switching | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5295
691 | F Switching | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5296
692 | F Switching | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5297
693 | F Switching | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5298
694 | F Switching | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5299
695 | F Switching | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5300
696 | F Switching | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5301
697 | F Switching | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5302
698 | F Switching | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5303
699 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 299
700 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 300
701 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 301
702 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 302
703 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 303
704 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 304
705 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 305
706 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 306 |  |  |  | AC CMR to be used
707 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 307
708 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 308
709 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10017
710 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10017
711 | Local Tr | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 309
712 | Local Tr | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 310
713 | Local Tr | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 311
714 | Local Tr | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 312
715 | Local Tr | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 313
716 | Local Tr | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 314
717 | Local Tr | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 315
718 | Local Tr | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 316
719 | Local Tr | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 317
720 | Local Tr | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 318
721 | Local Tr | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 319
722 | Local Tr | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 320
723 | Local Tr | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 321
724 | Local Tr | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 322
725 | Local Tr | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10018
726 | Local Tr | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10018
727 | Local Tr | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
728 | Local Tr | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
729 | Local Tr | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
730 | Local Tr | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5304
731 | Local Tr | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5305
732 | Local Tr | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5306
733 | Local Tr | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5307
734 | Local Tr | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5308
735 | Local Tr | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5309
736 | Local Tr | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5310
737 | Local Tr | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5311
738 | Local Tr | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5312
739 | Local Tr | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5313
740 | Local Tr | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5314
741 | Local Tr | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5315
742 | Local Tr | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5316
743 | Local Tr | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5317
744 | Local Tr | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5318
745 | Local Tr | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5319
746 | Local Tr | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5320
747 | Udyanchal lodge | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 323
748 | Udyanchal lodge | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 324
749 | Udyanchal lodge | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 325
750 | Udyanchal lodge | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 326
751 | Udyanchal lodge | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 327
752 | Udyanchal lodge | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 328
753 | Udyanchal lodge | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 329
754 | Udyanchal lodge | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 330
755 | Udyanchal lodge | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 331
756 | Udyanchal lodge | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 332
757 | Udyanchal lodge | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 333
758 | Udyanchal lodge | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 334
759 | Udyanchal lodge | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 335
760 | Udyanchal lodge | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 336
761 | Udyanchal lodge | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
762 | Udyanchal lodge | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
763 | Udyanchal lodge | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
764 | Udyanchal lodge | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
765 | Udyanchal lodge | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
766 | Udyanchal lodge | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5321
767 | Udyanchal lodge | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5322
768 | Udyanchal lodge | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5323
769 | Udyanchal lodge | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5324
770 | Udyanchal lodge | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5325
771 | Udyanchal lodge | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5326
772 | Udyanchal lodge | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5327
773 | Udyanchal lodge | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5328
774 | Udyanchal lodge | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5329
775 | Udyanchal lodge | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5330
776 | Udyanchal lodge | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5331
777 | Udyanchal lodge | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5332
778 | Udyanchal lodge | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5333
779 | Udyanchal lodge | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5334
780 | Udyanchal lodge | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5335
781 | Udyanchal lodge | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5336
782 | Udyanchal lodge | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5337
783 | From 33kV Tr-11 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 337
784 | From 33kV Tr-11 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 338
785 | From 33kV Tr-11 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 339
786 | From 33kV Tr-11 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 340
787 | From 33kV Tr-11 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 341
788 | From 33kV Tr-11 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 342
789 | From 33kV Tr-11 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 343
790 | From 33kV Tr-11 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 344
791 | From 33kV Tr-11 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 345
792 | From 33kV Tr-11 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 346
793 | From 33kV Tr-11 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 347
794 | From 33kV Tr-11 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 348
795 | From 33kV Tr-11 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 349
796 | From 33kV Tr-11 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
797 | From 33kV Tr-11 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
798 | From 33kV Tr-11 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
799 | From 33kV Tr-11 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13067
800 | From 33kV Tr-11 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13068
801 | From 33kV Tr-11 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5338
802 | From 33kV Tr-11 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5339
803 | From 33kV Tr-11 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5340
804 | From 33kV Tr-11 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5341
805 | From 33kV Tr-11 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5342
806 | From 33kV Tr-11 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5343
807 | From 33kV Tr-11 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5344
808 | From 33kV Tr-11 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5345
809 | From 33kV Tr-11 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5346
810 | From 33kV Tr-11 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5347
811 | From 33kV Tr-11 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5348
812 | From 33kV Tr-11 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5349
813 | From 33kV Tr-11 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5350
814 | From 33kV Tr-11 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5351
815 | From 33kV Tr-11 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5352
816 | From 33kV Tr-11 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5353
817 | From 33kV Tr-11 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5354
818 | Spare-2 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 350
819 | Spare-2 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 351
820 | Spare-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 352
821 | Spare-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 353
822 | Spare-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 354
823 | Spare-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 355
824 | Spare-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 356
825 | Spare-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 357
826 | Spare-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 358
827 | Spare-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 359
828 | Spare-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 360
829 | Spare-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 361
830 | Spare-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 362
831 | Spare-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 363
832 | Spare-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
833 | Spare-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
834 | Spare-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
835 | Spare-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
836 | Spare-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
837 | Spare-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5355
838 | Spare-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5356
839 | Spare-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5357
840 | Spare-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5358
841 | Spare-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5359
842 | Spare-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5360
843 | Spare-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5361
844 | Spare-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5362
845 | Spare-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5363
846 | Spare-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5364
847 | Spare-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5365
848 | Spare-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5366
849 | Spare-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5367
850 | Spare-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5368
851 | Spare-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5369
852 | Spare-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5370
853 | Spare-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5371
854 | G Switching | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 364
855 | G Switching | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 365
856 | G Switching | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 366
857 | G Switching | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 367
858 | G Switching | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 368
859 | G Switching | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 369
860 | G Switching | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 370
861 | G Switching | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 371
862 | G Switching | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 372
863 | G Switching | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 373
864 | G Switching | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 374
865 | G Switching | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 375
866 | G Switching | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 376
867 | G Switching | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 377
868 | G Switching | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10022
869 | G Switching | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10022
870 | G Switching | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
871 | G Switching | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
872 | G Switching | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
873 | G Switching | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5372
874 | G Switching | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5373
875 | G Switching | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5374
876 | G Switching | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5375
877 | G Switching | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5376
878 | G Switching | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5377
879 | G Switching | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5378
880 | G Switching | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5379
881 | G Switching | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5380
882 | G Switching | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5381
883 | G Switching | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5382
884 | G Switching | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5383
885 | G Switching | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5384
886 | G Switching | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5385
887 | G Switching | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5386
888 | G Switching | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5387
889 | G Switching | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5388
890 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close | SPI |  |  | Hard | CMR | 378
891 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open | SPI |  |  | Hard | CMR | 379
892 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 380
893 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 381
894 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 382
895 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 383
896 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 384
897 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 385 |  |  |  | AC CMR to be used
898 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 386
899 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 387
900 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10023
901 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10023
902 | Int conn Tr1 & Tr4 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 388
903 | Int conn Tr1 & Tr4 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 389
904 | Int conn Tr1 & Tr4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 390
905 | Int conn Tr1 & Tr4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 391
906 | Int conn Tr1 & Tr4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 392
907 | Int conn Tr1 & Tr4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 393
908 | Int conn Tr1 & Tr4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 394
909 | Int conn Tr1 & Tr4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 395
910 | Int conn Tr1 & Tr4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 396
911 | Int conn Tr1 & Tr4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 397
912 | Int conn Tr1 & Tr4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 398
913 | Int conn Tr1 & Tr4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 399
914 | Int conn Tr1 & Tr4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 400
915 | Int conn Tr1 & Tr4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
916 | Int conn Tr1 & Tr4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
917 | Int conn Tr1 & Tr4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
918 | Int conn Tr1 & Tr4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13076
919 | Int conn Tr1 & Tr4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13077
920 | Int conn Tr1 & Tr4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5389
921 | Int conn Tr1 & Tr4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5390
922 | Int conn Tr1 & Tr4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5391
923 | Int conn Tr1 & Tr4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5392
924 | Int conn Tr1 & Tr4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5393
925 | Int conn Tr1 & Tr4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5394
926 | Int conn Tr1 & Tr4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5395
927 | Int conn Tr1 & Tr4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5396
928 | Int conn Tr1 & Tr4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5397
929 | Int conn Tr1 & Tr4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5398
930 | Int conn Tr1 & Tr4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5399
931 | Int conn Tr1 & Tr4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5400
932 | Int conn Tr1 & Tr4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5401
933 | Int conn Tr1 & Tr4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5402
934 | Int conn Tr1 & Tr4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5403
935 | Int conn Tr1 & Tr4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5404
936 | Int conn Tr1 & Tr4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5405
937 | Spare-1 | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 401
938 | Spare-1 | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 402
939 | Spare-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 403
940 | Spare-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 404
941 | Spare-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 405
942 | Spare-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 406
943 | Spare-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 407
944 | Spare-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 408
945 | Spare-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 409
946 | Spare-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 410
947 | Spare-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 411
948 | Spare-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 412
949 | Spare-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 413
950 | Spare-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 414
951 | Spare-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10025
952 | Spare-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10025
953 | Spare-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
954 | Spare-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13079
955 | Spare-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13080
956 | Spare-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5406
957 | Spare-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5407
958 | Spare-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5408
959 | Spare-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5409
960 | Spare-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5410
961 | Spare-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5411
962 | Spare-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5412
963 | Spare-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5413
964 | Spare-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5414
965 | Spare-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5415
966 | Spare-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5416
967 | Spare-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5417
968 | Spare-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5418
969 | Spare-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5419
970 | Spare-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5420
971 | Spare-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5421
972 | Spare-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5422
973 | F-23 DS\S | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 415
974 | F-23 DS\S | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 416
975 | F-23 DS\S | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 417
976 | F-23 DS\S | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 418
977 | F-23 DS\S | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 419
978 | F-23 DS\S | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 420
979 | F-23 DS\S | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 421
980 | F-23 DS\S | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 422
981 | F-23 DS\S | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 423
982 | F-23 DS\S | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 424
983 | F-23 DS\S | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 425
984 | F-23 DS\S | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 426
985 | F-23 DS\S | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 427
986 | F-23 DS\S | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 428
987 | F-23 DS\S | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
988 | F-23 DS\S | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
989 | F-23 DS\S | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
990 | F-23 DS\S | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13082
991 | F-23 DS\S | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13083
992 | F-23 DS\S | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5423
993 | F-23 DS\S | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5424
994 | F-23 DS\S | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5425
995 | F-23 DS\S | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5426
996 | F-23 DS\S | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5427
997 | F-23 DS\S | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5428
998 | F-23 DS\S | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5429
999 | F-23 DS\S | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5430
1000 | F-23 DS\S | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5431
1001 | F-23 DS\S | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5432
1002 | F-23 DS\S | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5433
1003 | F-23 DS\S | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5434
1004 | F-23 DS\S | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5435
1005 | F-23 DS\S | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5436
1006 | F-23 DS\S | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5437
1007 | F-23 DS\S | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5438
1008 | F-23 DS\S | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5439
1009 | E-SU\STN | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 429
1010 | E-SU\STN | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 430
1011 | E-SU\STN | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 431
1012 | E-SU\STN | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 432
1013 | E-SU\STN | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 433
1014 | E-SU\STN | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 434
1015 | E-SU\STN | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 435
1016 | E-SU\STN | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 436
1017 | E-SU\STN | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 437
1018 | E-SU\STN | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 438
1019 | E-SU\STN | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 439
1020 | E-SU\STN | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 440
1021 | E-SU\STN | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 441
1022 | E-SU\STN | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 442
1023 | E-SU\STN | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10027
1024 | E-SU\STN | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10027
1025 | E-SU\STN | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1026 | E-SU\STN | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1027 | E-SU\STN | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13086
1028 | E-SU\STN | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5440
1029 | E-SU\STN | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5441
1030 | E-SU\STN | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5442
1031 | E-SU\STN | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5443
1032 | E-SU\STN | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5444
1033 | E-SU\STN | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5445
1034 | E-SU\STN | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5446
1035 | E-SU\STN | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5447
1036 | E-SU\STN | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5448
1037 | E-SU\STN | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5449
1038 | E-SU\STN | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5450
1039 | E-SU\STN | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5451
1040 | E-SU\STN | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5452
1041 | E-SU\STN | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5453
1042 | E-SU\STN | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5454
1043 | E-SU\STN | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5455
1044 | E-SU\STN | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5456
1045 | Tr-1 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 443
1046 | Tr-1 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 444
1047 | Tr-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 445
1048 | Tr-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 446
1049 | Tr-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 447
1050 | Tr-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 448
1051 | Tr-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 449
1052 | Tr-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 450
1053 | Tr-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 451
1054 | Tr-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 452
1055 | Tr-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 453
1056 | Tr-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 454
1057 | Tr-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 455
1058 | Tr-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10028
1059 | Tr-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10028
1060 | Tr-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1061 | Tr-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1062 | Tr-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13089
1063 | Tr-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5457
1064 | Tr-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5458
1065 | Tr-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5459
1066 | Tr-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5460
1067 | Tr-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5461
1068 | Tr-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5462
1069 | Tr-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5463
1070 | Tr-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5464
1071 | Tr-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5465
1072 | Tr-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5466
1073 | Tr-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5467
1074 | Tr-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5468
1075 | Tr-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5469
1076 | Tr-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5470
1077 | Tr-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5471
1078 | Tr-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5472
1079 | Tr-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5473
1080 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 456
1081 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 457
1082 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 458
1083 | Int Conn Tr4 & Tr1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 459
1084 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 460
1085 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 461
1086 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 462
1087 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 463
1088 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 464
1089 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 465
1090 | Int Conn Tr4 & Tr1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 466
1091 | Int Conn Tr4 & Tr1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 467
1092 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 468
1093 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10029
1094 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10029
1095 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1096 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1097 | Int Conn Tr4 & Tr1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13092
1098 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5474
1099 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5475
1100 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5476
1101 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5477
1102 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5478
1103 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5479
1104 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5480
1105 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5481
1106 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5482
1107 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5483
1108 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5484
1109 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5485
1110 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5486
1111 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5487
1112 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5488
1113 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5489
1114 | Int Conn Tr4 & Tr1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5490
1115 | Stadium | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 469
1116 | Stadium | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 470
1117 | Stadium | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 471
1118 | Stadium | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 472
1119 | Stadium | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 473
1120 | Stadium | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 474
1121 | Stadium | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 475
1122 | Stadium | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 476
1123 | Stadium | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 477
1124 | Stadium | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 478
1125 | Stadium | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 479
1126 | Stadium | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 480
1127 | Stadium | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 481
1128 | Stadium | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 482
1129 | Stadium | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10030
1130 | Stadium | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10030
1131 | Stadium | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13093
1132 | Stadium | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13094
1133 | Stadium | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13095
1134 | Stadium | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5491
1135 | Stadium | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5492
1136 | Stadium | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5493
1137 | Stadium | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5494
1138 | Stadium | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5495
1139 | Stadium | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5496
1140 | Stadium | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5497
1141 | Stadium | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5498
1142 | Stadium | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5499
1143 | Stadium | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5500
1144 | Stadium | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5501
1145 | Stadium | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5502
1146 | Stadium | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5503
1147 | Stadium | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5504
1148 | Stadium | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5505
1149 | Stadium | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5506
1150 | Stadium | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5507
1151 | Tr-4 | 11kV | Incomer | Circuit breaker Close | SPI |  |  | Soft | IED | 483
1152 | Tr-4 | 11kV | Incomer | Circuit breaker Open | SPI |  |  | Soft | IED | 484
1153 | Tr-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 485
1154 | Tr-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 486
1155 | Tr-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 487
1156 | Tr-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 488
1157 | Tr-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 489
1158 | Tr-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 490
1159 | Tr-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 491
1160 | Tr-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 492
1161 | Tr-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 493
1162 | Tr-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 494
1163 | Tr-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 495
1164 | Tr-4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10031
1165 | Tr-4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10031
1166 | Tr-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13096
1167 | Tr-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13097
1168 | Tr-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13098
1169 | Tr-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5508
1170 | Tr-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5509
1171 | Tr-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5510
1172 | Tr-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5511
1173 | Tr-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5512
1174 | Tr-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5513
1175 | Tr-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5514
1176 | Tr-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5515
1177 | Tr-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5516
1178 | Tr-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5517
1179 | Tr-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5518
1180 | Tr-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5519
1181 | Tr-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5520
1182 | Tr-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5521
1183 | Tr-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5522
1184 | Tr-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5523
1185 | Tr-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5524
1186 | Bidyut Bhawan | 11kV | Outgoing | Circuit breaker Close | SPI |  |  | Soft | IED | 496
1187 | Bidyut Bhawan | 11kV | Outgoing | Circuit breaker Open | SPI |  |  | Soft | IED | 497
1188 | Bidyut Bhawan | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 498
1189 | Bidyut Bhawan | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 499
1190 | Bidyut Bhawan | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 500
1191 | Bidyut Bhawan | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 501
1192 | Bidyut Bhawan | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 502
1193 | Bidyut Bhawan | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 503
1194 | Bidyut Bhawan | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 504
1195 | Bidyut Bhawan | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 505
1196 | Bidyut Bhawan | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 506
1197 | Bidyut Bhawan | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 507
1198 | Bidyut Bhawan | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 508
1199 | Bidyut Bhawan | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 509
1200 | Bidyut Bhawan | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10032
1201 | Bidyut Bhawan | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10032
1202 | Bidyut Bhawan | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13099
1203 | Bidyut Bhawan | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13100
1204 | Bidyut Bhawan | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13101
1205 | Bidyut Bhawan | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5525
1206 | Bidyut Bhawan | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5526
1207 | Bidyut Bhawan | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5527
1208 | Bidyut Bhawan | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5528
1209 | Bidyut Bhawan | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5529
1210 | Bidyut Bhawan | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5530
1211 | Bidyut Bhawan | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5531
1212 | Bidyut Bhawan | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5532
1213 | Bidyut Bhawan | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5533
1214 | Bidyut Bhawan | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5534
1215 | Bidyut Bhawan | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5535
1216 | Bidyut Bhawan | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5536
1217 | Bidyut Bhawan | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5537
1218 | Bidyut Bhawan | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5538
1219 | Bidyut Bhawan | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5539
1220 | Bidyut Bhawan | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5540
1221 | Bidyut Bhawan | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5541
1222 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5542
1223 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5543
1224 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5544
1225 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5545
1226 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5546
1227 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5547
1228 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5548