## Signal List
SCADA/Advanced Distribution Management System (ADMS)
SL.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC Charger-1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC Charger-1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC Charger-1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC Charger-2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC Charger-2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC Charger-2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | DUMMY CB | 3000
23 | Sub-Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | DUMMY CB | 10000
24 | Sub-Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | Transformer-4 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 112
209 | Transformer-4 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 113
210 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 114
211 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 115
212 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 116
213 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 117
214 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 118
215 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 119
216 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 120
217 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 121
218 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 122
219 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 123
220 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 124
221 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 125
222 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 126
223 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 127
224 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 128
225 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 129
226 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 130
227 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 131
228 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 132
229 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 133
230 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 134
231 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 135
232 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
233 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
234 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
235 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
236 | Transformer-4 | 33kV | Transformer | Circuit Breaker Close Command | DPC |  |  | Soft | IED1 | 10004
237 | Transformer-4 | 33kV | Transformer | Circuit Breaker Open Command | DPC |  |  | Soft | IED1 | 10004
238 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5068
239 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5069
240 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5070
241 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5071
242 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5072
243 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5073
244 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5074
245 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5075
246 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5076
247 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5077
248 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5078
249 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5079
250 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5080
251 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5081
252 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5082
253 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
254 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
255 | Transformer-4 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 136
256 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 137
257 | Transformer-4 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 138 |  |  |  | AC CMR to be used
258 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 139
259 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 140
260 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 141
261 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 142
262 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 143
263 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
264 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
265 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5085
266 | Transformer-4 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5086
267 | Transformer-4 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5087
268 | Transformer-5 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 144
269 | Transformer-5 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 145
270 | Transformer-5 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 146
271 | Transformer-5 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 147
272 | Transformer-5 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 148
273 | Transformer-5 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 149
274 | Transformer-5 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 150
275 | Transformer-5 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 151
276 | Transformer-5 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 152
277 | Transformer-5 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 153
278 | Transformer-5 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 154
279 | Transformer-5 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 155
280 | Transformer-5 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 156
281 | Transformer-5 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 157
282 | Transformer-5 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 158
283 | Transformer-5 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 159
284 | Transformer-5 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 160
285 | Transformer-5 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 161
286 | Transformer-5 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 162
287 | Transformer-5 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 163
288 | Transformer-5 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 164
289 | Transformer-5 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 165
290 | Transformer-5 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 166
291 | Transformer-5 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 167
292 | Transformer-5 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13024
293 | Transformer-5 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13025
294 | Transformer-5 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13026
295 | Transformer-5 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13027
296 | Transformer-5 | 33kV | Transformer | Circuit Breaker Close Command | DPC |  |  | Soft | IED1 | 10005
297 | Transformer-5 | 33kV | Transformer | Circuit Breaker Open Command | DPC |  |  | Soft | IED1 | 10005
298 | Transformer-5 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5088
299 | Transformer-5 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5089
300 | Transformer-5 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5090
301 | Transformer-5 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5091
302 | Transformer-5 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5092
303 | Transformer-5 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5093
304 | Transformer-5 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5094
305 | Transformer-5 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5095
306 | Transformer-5 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5096
307 | Transformer-5 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5097
308 | Transformer-5 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5098
309 | Transformer-5 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5099
310 | Transformer-5 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5100
311 | Transformer-5 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5101
312 | Transformer-5 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5102
313 | Transformer-5 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5103
314 | Transformer-5 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5104
315 | Transformer-5 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 168
316 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 169
317 | Transformer-5 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 170 |  |  |  | AC CMR to be used
318 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 171
319 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 172
320 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 173
321 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 174
322 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 175
323 | Transformer-5 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13028
324 | Transformer-5 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13029
325 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5105
326 | Transformer-5 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5106
327 | Transformer-5 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5107
328 | Stadium Tr | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 176
329 | Stadium Tr | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 177
330 | Stadium Tr | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 178
331 | Stadium Tr | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 179
332 | Stadium Tr | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 180
333 | Stadium Tr | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 181
334 | Stadium Tr | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 182
335 | Stadium Tr | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 183
336 | Stadium Tr | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 184
337 | Stadium Tr | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 185
338 | Stadium Tr | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 186
339 | Stadium Tr | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 187
340 | Stadium Tr | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
341 | Stadium Tr | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13031
342 | Stadium Tr | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13032
343 | Stadium Tr | 33kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10006
344 | Stadium Tr | 33kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10006
345 | Stadium Tr | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5108
346 | Stadium Tr | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5109
347 | Stadium Tr | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5110
348 | Stadium Tr | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5111
349 | Stadium Tr | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5112
350 | Stadium Tr | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5113
351 | Stadium Tr | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5114
352 | Stadium Tr | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5115
353 | Stadium Tr | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5116
354 | Stadium Tr | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5117
355 | Stadium Tr | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5118
356 | Stadium Tr | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5119
357 | Stadium Tr | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5120
358 | Stadium Tr | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5121
359 | Stadium Tr | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5122
360 | Stadium Tr | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5123
361 | Stadium Tr | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5124
362 | Stadium Tr | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5125
363 | Stadium Tr | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5126
364 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 188
365 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 189
366 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 190
367 | M3-M5 Inter connector | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 191
368 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 192
369 | M3-M5 Inter connector | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 193
370 | M3-M5 Inter connector | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 194
371 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 195
372 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 196
373 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 197
374 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 198
375 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 199
376 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
377 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
378 | M3-M5 Inter connector | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13035
379 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10007
380 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10007
381 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5127
382 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5128
383 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5129
384 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5130
385 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5131
386 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5132
387 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5133
388 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5134
389 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5135
390 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5136
391 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5137
392 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5138
393 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5139
394 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5140
395 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5141
396 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5142
397 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5143
398 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5144
399 | M3-M5 Inter connector | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5145
400 | Hyatt Asian Hotel | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 200
401 | Hyatt Asian Hotel | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 201
402 | Hyatt Asian Hotel | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 202
403 | Hyatt Asian Hotel | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 203
404 | Hyatt Asian Hotel | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 204
405 | Hyatt Asian Hotel | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 205
406 | Hyatt Asian Hotel | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 206
407 | Hyatt Asian Hotel | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 207
408 | Hyatt Asian Hotel | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 208
409 | Hyatt Asian Hotel | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 209
410 | Hyatt Asian Hotel | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 210
411 | Hyatt Asian Hotel | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 211
412 | Hyatt Asian Hotel | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
413 | Hyatt Asian Hotel | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13037
414 | Hyatt Asian Hotel | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13038
415 | Hyatt Asian Hotel | 33kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10008
416 | Hyatt Asian Hotel | 33kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10008
417 | Hyatt Asian Hotel | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5146
418 | Hyatt Asian Hotel | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5147
419 | Hyatt Asian Hotel | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5148
420 | Hyatt Asian Hotel | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5149
421 | Hyatt Asian Hotel | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5150
422 | Hyatt Asian Hotel | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5151
423 | Hyatt Asian Hotel | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5152
424 | Hyatt Asian Hotel | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5153
425 | Hyatt Asian Hotel | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5154
426 | Hyatt Asian Hotel | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5155
427 | Hyatt Asian Hotel | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5156
428 | Hyatt Asian Hotel | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5157
429 | Hyatt Asian Hotel | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5158
430 | Hyatt Asian Hotel | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5159
431 | Hyatt Asian Hotel | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5160
432 | Hyatt Asian Hotel | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5161
433 | Hyatt Asian Hotel | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5162
434 | Hyatt Asian Hotel | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5163
435 | Hyatt Asian Hotel | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5164
436 | GIS fdr-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 212
437 | GIS fdr-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 213
438 | GIS fdr-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 214
439 | GIS fdr-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 215
440 | GIS fdr-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 216
441 | GIS fdr-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 217
442 | GIS fdr-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 218
443 | GIS fdr-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 219
444 | GIS fdr-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 220
445 | GIS fdr-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 221
446 | GIS fdr-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 222
447 | GIS fdr-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 223
448 | GIS fdr-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
449 | GIS fdr-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13040
450 | GIS fdr-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13041
451 | GIS fdr-1 | 33kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10009
452 | GIS fdr-1 | 33kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10009
453 | GIS fdr-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5165
454 | GIS fdr-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5166
455 | GIS fdr-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5167
456 | GIS fdr-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5168
457 | GIS fdr-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5169
458 | GIS fdr-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5170
459 | GIS fdr-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5171
460 | GIS fdr-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5172
461 | GIS fdr-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5173
462 | GIS fdr-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5174
463 | GIS fdr-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5175
464 | GIS fdr-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5176
465 | GIS fdr-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5177
466 | GIS fdr-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5178
467 | GIS fdr-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5179
468 | GIS fdr-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5180
469 | GIS fdr-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5181
470 | GIS fdr-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5182
471 | GIS fdr-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5183
472 | GIS fdr-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 224
473 | GIS fdr-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 225
474 | GIS fdr-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 226
475 | GIS fdr-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 227
476 | GIS fdr-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 228
477 | GIS fdr-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 229
478 | GIS fdr-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 230
479 | GIS fdr-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 231
480 | GIS fdr-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 232
481 | GIS fdr-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 233
482 | GIS fdr-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 234
483 | GIS fdr-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 235
484 | GIS fdr-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
485 | GIS fdr-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13043
486 | GIS fdr-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13044
487 | GIS fdr-2 | 33kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10010
488 | GIS fdr-2 | 33kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10010
489 | GIS fdr-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5184
490 | GIS fdr-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5185
491 | GIS fdr-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5186
492 | GIS fdr-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5187
493 | GIS fdr-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5188
494 | GIS fdr-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5189
495 | GIS fdr-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5190
496 | GIS fdr-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5191
497 | GIS fdr-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5192
498 | GIS fdr-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5193
499 | GIS fdr-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5194
500 | GIS fdr-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5195
501 | GIS fdr-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5196
502 | GIS fdr-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5197
503 | GIS fdr-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5198
504 | GIS fdr-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5199
505 | GIS fdr-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5200
506 | GIS fdr-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5201
507 | GIS fdr-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5202
508 | Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 236
509 | Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 237
510 | Salt lake fdr-1 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 238
511 | Salt lake fdr-1 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 239
512 | Salt lake fdr-1 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 240
513 | Salt lake fdr-1 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 241
514 | Salt lake fdr-1 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 242
515 | Salt lake fdr-1 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 243
516 | Salt lake fdr-1 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 244
517 | Salt lake fdr-1 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 245
518 | Salt lake fdr-1 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 246
519 | Salt lake fdr-1 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 247
520 | Salt lake fdr-1 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
521 | Salt lake fdr-1 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13046
522 | Salt lake fdr-1 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13047
523 | Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10011
524 | Salt lake fdr-1 | 33kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10011
525 | Salt lake fdr-1 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5203
526 | Salt lake fdr-1 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5204
527 | Salt lake fdr-1 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5205
528 | Salt lake fdr-1 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5206
529 | Salt lake fdr-1 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5207
530 | Salt lake fdr-1 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5208
531 | Salt lake fdr-1 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5209
532 | Salt lake fdr-1 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5210
533 | Salt lake fdr-1 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5211
534 | Salt lake fdr-1 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5212
535 | Salt lake fdr-1 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5213
536 | Salt lake fdr-1 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5214
537 | Salt lake fdr-1 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5215
538 | Salt lake fdr-1 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5216
539 | Salt lake fdr-1 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5217
540 | Salt lake fdr-1 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5218
541 | Salt lake fdr-1 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5219
542 | Salt lake fdr-1 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5220
543 | Salt lake fdr-1 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5221
544 | Salt lake fdr-2 | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 248
545 | Salt lake fdr-2 | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 249
546 | Salt lake fdr-2 | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 250
547 | Salt lake fdr-2 | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 251
548 | Salt lake fdr-2 | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 252
549 | Salt lake fdr-2 | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 253
550 | Salt lake fdr-2 | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 254
551 | Salt lake fdr-2 | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 255
552 | Salt lake fdr-2 | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 256
553 | Salt lake fdr-2 | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 257
554 | Salt lake fdr-2 | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 258
555 | Salt lake fdr-2 | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 259
556 | Salt lake fdr-2 | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
557 | Salt lake fdr-2 | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13049
558 | Salt lake fdr-2 | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13050
559 | Salt lake fdr-2 | 33kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10012
560 | Salt lake fdr-2 | 33kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10012
561 | Salt lake fdr-2 | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5222
562 | Salt lake fdr-2 | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5223
563 | Salt lake fdr-2 | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5224
564 | Salt lake fdr-2 | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5225
565 | Salt lake fdr-2 | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5226
566 | Salt lake fdr-2 | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5227
567 | Salt lake fdr-2 | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5228
568 | Salt lake fdr-2 | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5229
569 | Salt lake fdr-2 | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5230
570 | Salt lake fdr-2 | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5231
571 | Salt lake fdr-2 | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5232
572 | Salt lake fdr-2 | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5233
573 | Salt lake fdr-2 | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5234
574 | Salt lake fdr-2 | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5235
575 | Salt lake fdr-2 | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5236
576 | Salt lake fdr-2 | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5237
577 | Salt lake fdr-2 | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5238
578 | Salt lake fdr-2 | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5239
579 | Salt lake fdr-2 | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5240
580 | Incomer STD.GIS | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 260
581 | Incomer STD.GIS | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 261
582 | Incomer STD.GIS | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 262
583 | Incomer STD.GIS | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 263
584 | Incomer STD.GIS | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 264
585 | Incomer STD.GIS | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 265
586 | Incomer STD.GIS | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 266
587 | Incomer STD.GIS | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 267
588 | Incomer STD.GIS | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 268
589 | Incomer STD.GIS | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 269
590 | Incomer STD.GIS | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 270
591 | Incomer STD.GIS | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 271
592 | Incomer STD.GIS | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 272
593 | Incomer STD.GIS | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10013
594 | Incomer STD.GIS | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10013
595 | Incomer STD.GIS | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
596 | Incomer STD.GIS | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13052
597 | Incomer STD.GIS | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13053
598 | Incomer STD.GIS | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5241
599 | Incomer STD.GIS | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5242
600 | Incomer STD.GIS | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5243
601 | Incomer STD.GIS | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5244
602 | Incomer STD.GIS | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5245
603 | Incomer STD.GIS | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5246
604 | Incomer STD.GIS | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5247
605 | Incomer STD.GIS | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5248
606 | Incomer STD.GIS | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5249
607 | Incomer STD.GIS | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5250
608 | Incomer STD.GIS | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5251
609 | Incomer STD.GIS | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5252
610 | Incomer STD.GIS | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5253
611 | Incomer STD.GIS | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5254
612 | Incomer STD.GIS | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5255
613 | Incomer STD.GIS | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5256
614 | Incomer STD.GIS | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5257
615 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 273
616 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 274
617 | Bus Coupler-4 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 275
618 | Bus Coupler-4 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 276
619 | Bus Coupler-4 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 277
620 | Bus Coupler-4 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 278
621 | Bus Coupler-4 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 279
622 | Bus Coupler-4 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 280 |  |  |  | AC CMR to be used
623 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 281
624 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 282
625 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Close Command | DPC |  |  | Hard | HDR | 10014
626 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Open Command | DPC |  |  | Hard | HDR | 10014
627 | Tr-4 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 283
628 | Tr-4 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 284
629 | Tr-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 285
630 | Tr-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 286
631 | Tr-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 287
632 | Tr-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 288
633 | Tr-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 289
634 | Tr-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 290
635 | Tr-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 291
636 | Tr-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 292
637 | Tr-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 293
638 | Tr-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 294
639 | Tr-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 295
640 | Tr-4 | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10015
641 | Tr-4 | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10015
642 | Tr-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
643 | Tr-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13055
644 | Tr-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13056
645 | Tr-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5258
646 | Tr-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5259
647 | Tr-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5260
648 | Tr-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5261
649 | Tr-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5262
650 | Tr-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5263
651 | Tr-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5264
652 | Tr-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5265
653 | Tr-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5266
654 | Tr-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5267
655 | Tr-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5268
656 | Tr-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5269
657 | Tr-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5270
658 | Tr-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5271
659 | Tr-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5272
660 | Tr-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5273
661 | Tr-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5274
662 | Q.S\STN | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 296
663 | Q.S\STN | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 297
664 | Q.S\STN | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 298
665 | Q.S\STN | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 299
666 | Q.S\STN | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 300
667 | Q.S\STN | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 301
668 | Q.S\STN | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 302
669 | Q.S\STN | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 303
670 | Q.S\STN | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 304
671 | Q.S\STN | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 305
672 | Q.S\STN | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 306
673 | Q.S\STN | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 307
674 | Q.S\STN | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 308
675 | Q.S\STN | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 309
676 | Q.S\STN | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10016
677 | Q.S\STN | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10016
678 | Q.S\STN | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
679 | Q.S\STN | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13058
680 | Q.S\STN | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13059
681 | Q.S\STN | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5275
682 | Q.S\STN | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5276
683 | Q.S\STN | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5277
684 | Q.S\STN | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5278
685 | Q.S\STN | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5279
686 | Q.S\STN | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5280
687 | Q.S\STN | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5281
688 | Q.S\STN | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5282
689 | Q.S\STN | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5283
690 | Q.S\STN | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5284
691 | Q.S\STN | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5285
692 | Q.S\STN | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5286
693 | Q.S\STN | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5287
694 | Q.S\STN | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5288
695 | Q.S\STN | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5289
696 | Q.S\STN | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5290
697 | Q.S\STN | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5291
698 | PDCL | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 310
699 | PDCL | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 311
700 | PDCL | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 312
701 | PDCL | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 313
702 | PDCL | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 314
703 | PDCL | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 315
704 | PDCL | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 316
705 | PDCL | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 317
706 | PDCL | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 318
707 | PDCL | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 319
708 | PDCL | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 320
709 | PDCL | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 321
710 | PDCL | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 322
711 | PDCL | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 323
712 | PDCL | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10017
713 | PDCL | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10017
714 | PDCL | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
715 | PDCL | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
716 | PDCL | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
717 | PDCL | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5292
718 | PDCL | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5293
719 | PDCL | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5294
720 | PDCL | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5295
721 | PDCL | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5296
722 | PDCL | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5297
723 | PDCL | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5298
724 | PDCL | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5299
725 | PDCL | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5300
726 | PDCL | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5301
727 | PDCL | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5302
728 | PDCL | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5303
729 | PDCL | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5304
730 | PDCL | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5305
731 | PDCL | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5306
732 | PDCL | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5307
733 | PDCL | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5308
734 | NIH Hostel | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 324
735 | NIH Hostel | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 325
736 | NIH Hostel | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 326
737 | NIH Hostel | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 327
738 | NIH Hostel | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 328
739 | NIH Hostel | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 329
740 | NIH Hostel | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 330
741 | NIH Hostel | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 331
742 | NIH Hostel | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 332
743 | NIH Hostel | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 333
744 | NIH Hostel | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 334
745 | NIH Hostel | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 335
746 | NIH Hostel | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 336
747 | NIH Hostel | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 337
748 | NIH Hostel | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10018
749 | NIH Hostel | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10018
750 | NIH Hostel | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
751 | NIH Hostel | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
752 | NIH Hostel | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
753 | NIH Hostel | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5309
754 | NIH Hostel | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5310
755 | NIH Hostel | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5311
756 | NIH Hostel | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5312
757 | NIH Hostel | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5313
758 | NIH Hostel | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5314
759 | NIH Hostel | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5315
760 | NIH Hostel | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5316
761 | NIH Hostel | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5317
762 | NIH Hostel | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5318
763 | NIH Hostel | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5319
764 | NIH Hostel | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5320
765 | NIH Hostel | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5321
766 | NIH Hostel | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5322
767 | NIH Hostel | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5323
768 | NIH Hostel | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5324
769 | NIH Hostel | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5325
770 | I Feeder | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 338
771 | I Feeder | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 339
772 | I Feeder | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 340
773 | I Feeder | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 341
774 | I Feeder | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 342
775 | I Feeder | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 343
776 | I Feeder | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 344
777 | I Feeder | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 345
778 | I Feeder | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 346
779 | I Feeder | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 347
780 | I Feeder | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 348
781 | I Feeder | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 349
782 | I Feeder | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 350
783 | I Feeder | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 351
784 | I Feeder | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10019
785 | I Feeder | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10019
786 | I Feeder | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
787 | I Feeder | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
788 | I Feeder | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
789 | I Feeder | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5326
790 | I Feeder | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5327
791 | I Feeder | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5328
792 | I Feeder | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5329
793 | I Feeder | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5330
794 | I Feeder | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5331
795 | I Feeder | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5332
796 | I Feeder | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5333
797 | I Feeder | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5334
798 | I Feeder | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5335
799 | I Feeder | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5336
800 | I Feeder | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5337
801 | I Feeder | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5338
802 | I Feeder | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5339
803 | I Feeder | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5340
804 | I Feeder | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5341
805 | I Feeder | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5342
806 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 352
807 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 353
808 | Bus Coupler-3 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 354
809 | Bus Coupler-3 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 355
810 | Bus Coupler-3 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 356
811 | Bus Coupler-3 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 357
812 | Bus Coupler-3 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 358
813 | Bus Coupler-3 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 359 |  |  |  | AC CMR to be used
814 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 360
815 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 361
816 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Close Command | DPC |  |  | Hard | HDR | 10020
817 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Open Command | DPC |  |  | Hard | HDR | 10020
818 | H Feeder | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 362
819 | H Feeder | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 363
820 | H Feeder | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 364
821 | H Feeder | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 365
822 | H Feeder | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 366
823 | H Feeder | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 367
824 | H Feeder | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 368
825 | H Feeder | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 369
826 | H Feeder | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 370
827 | H Feeder | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 371
828 | H Feeder | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 372
829 | H Feeder | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 373
830 | H Feeder | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 374
831 | H Feeder | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 375
832 | H Feeder | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10021
833 | H Feeder | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10021
834 | H Feeder | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
835 | H Feeder | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
836 | H Feeder | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
837 | H Feeder | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5343
838 | H Feeder | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5344
839 | H Feeder | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5345
840 | H Feeder | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5346
841 | H Feeder | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5347
842 | H Feeder | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5348
843 | H Feeder | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5349
844 | H Feeder | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5350
845 | H Feeder | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5351
846 | H Feeder | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5352
847 | H Feeder | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5353
848 | H Feeder | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5354
849 | H Feeder | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5355
850 | H Feeder | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5356
851 | H Feeder | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5357
852 | H Feeder | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5358
853 | H Feeder | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5359
854 | Ladies Hostel | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 376
855 | Ladies Hostel | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 377
856 | Ladies Hostel | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 378
857 | Ladies Hostel | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 379
858 | Ladies Hostel | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 380
859 | Ladies Hostel | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 381
860 | Ladies Hostel | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 382
861 | Ladies Hostel | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 383
862 | Ladies Hostel | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 384
863 | Ladies Hostel | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 385
864 | Ladies Hostel | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 386
865 | Ladies Hostel | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 387
866 | Ladies Hostel | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 388
867 | Ladies Hostel | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 389
868 | Ladies Hostel | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10022
869 | Ladies Hostel | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10022
870 | Ladies Hostel | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
871 | Ladies Hostel | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
872 | Ladies Hostel | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
873 | Ladies Hostel | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5360
874 | Ladies Hostel | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5361
875 | Ladies Hostel | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5362
876 | Ladies Hostel | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5363
877 | Ladies Hostel | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5364
878 | Ladies Hostel | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5365
879 | Ladies Hostel | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5366
880 | Ladies Hostel | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5367
881 | Ladies Hostel | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5368
882 | Ladies Hostel | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5369
883 | Ladies Hostel | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5370
884 | Ladies Hostel | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5371
885 | Ladies Hostel | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5372
886 | Ladies Hostel | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5373
887 | Ladies Hostel | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5374
888 | Ladies Hostel | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5375
889 | Ladies Hostel | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5376
890 | kolkata University | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 390
891 | kolkata University | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 391
892 | kolkata University | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 392
893 | kolkata University | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 393
894 | kolkata University | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 394
895 | kolkata University | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 395
896 | kolkata University | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 396
897 | kolkata University | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 397
898 | kolkata University | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 398
899 | kolkata University | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 399
900 | kolkata University | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 400
901 | kolkata University | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 401
902 | kolkata University | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 402
903 | kolkata University | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 403
904 | kolkata University | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10023
905 | kolkata University | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10023
906 | kolkata University | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
907 | kolkata University | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13076
908 | kolkata University | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13077
909 | kolkata University | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5377
910 | kolkata University | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5378
911 | kolkata University | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5379
912 | kolkata University | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5380
913 | kolkata University | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5381
914 | kolkata University | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5382
915 | kolkata University | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5383
916 | kolkata University | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5384
917 | kolkata University | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5385
918 | kolkata University | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5386
919 | kolkata University | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5387
920 | kolkata University | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5388
921 | kolkata University | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5389
922 | kolkata University | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5390
923 | kolkata University | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5391
924 | kolkata University | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5392
925 | kolkata University | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5393
926 | Tr-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 404
927 | Tr-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 405
928 | Tr-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 406
929 | Tr-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 407
930 | Tr-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 408
931 | Tr-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 409
932 | Tr-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 410
933 | Tr-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 411
934 | Tr-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 412
935 | Tr-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 413
936 | Tr-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 414
937 | Tr-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 415
938 | Tr-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 416
939 | Tr-3 | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10024
940 | Tr-3 | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10024
941 | Tr-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
942 | Tr-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13079
943 | Tr-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13080
944 | Tr-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5394
945 | Tr-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5395
946 | Tr-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5396
947 | Tr-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5397
948 | Tr-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5398
949 | Tr-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5399
950 | Tr-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5400
951 | Tr-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5401
952 | Tr-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5402
953 | Tr-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5403
954 | Tr-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5404
955 | Tr-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5405
956 | Tr-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5406
957 | Tr-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5407
958 | Tr-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5408
959 | Tr-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5409
960 | Tr-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5410
961 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 417
962 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 418
963 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 419
964 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 420
965 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 421
966 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 422
967 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 423
968 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 424 |  |  |  | AC CMR to be used
969 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 425
970 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 426
971 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close Command | DPC |  |  | Hard | HDR | 10025
972 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open Command | DPC |  |  | Hard | HDR | 10025
973 | Shanti nagar | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 427
974 | Shanti nagar | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 428
975 | Shanti nagar | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 429
976 | Shanti nagar | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 430
977 | Shanti nagar | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 431
978 | Shanti nagar | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 432
979 | Shanti nagar | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 433
980 | Shanti nagar | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 434
981 | Shanti nagar | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 435
982 | Shanti nagar | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 436
983 | Shanti nagar | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 437
984 | Shanti nagar | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 438
985 | Shanti nagar | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 439
986 | Shanti nagar | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 440
987 | Shanti nagar | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10026
988 | Shanti nagar | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10026
989 | Shanti nagar | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
990 | Shanti nagar | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13082
991 | Shanti nagar | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13083
992 | Shanti nagar | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5411
993 | Shanti nagar | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5412
994 | Shanti nagar | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5413
995 | Shanti nagar | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5414
996 | Shanti nagar | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5415
997 | Shanti nagar | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5416
998 | Shanti nagar | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5417
999 | Shanti nagar | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5418
1000 | Shanti nagar | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5419
1001 | Shanti nagar | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5420
1002 | Shanti nagar | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5421
1003 | Shanti nagar | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5422
1004 | Shanti nagar | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5423
1005 | Shanti nagar | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5424
1006 | Shanti nagar | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5425
1007 | Shanti nagar | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5426
1008 | Shanti nagar | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5427
1009 | Moulana abul kalam | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 441
1010 | Moulana abul kalam | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 442
1011 | Moulana abul kalam | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 443
1012 | Moulana abul kalam | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 444
1013 | Moulana abul kalam | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 445
1014 | Moulana abul kalam | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 446
1015 | Moulana abul kalam | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 447
1016 | Moulana abul kalam | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 448
1017 | Moulana abul kalam | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 449
1018 | Moulana abul kalam | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 450
1019 | Moulana abul kalam | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 451
1020 | Moulana abul kalam | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 452
1021 | Moulana abul kalam | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 453
1022 | Moulana abul kalam | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 454
1023 | Moulana abul kalam | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10027
1024 | Moulana abul kalam | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10027
1025 | Moulana abul kalam | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1026 | Moulana abul kalam | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1027 | Moulana abul kalam | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13086
1028 | Moulana abul kalam | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5428
1029 | Moulana abul kalam | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5429
1030 | Moulana abul kalam | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5430
1031 | Moulana abul kalam | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5431
1032 | Moulana abul kalam | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5432
1033 | Moulana abul kalam | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5433
1034 | Moulana abul kalam | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5434
1035 | Moulana abul kalam | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5435
1036 | Moulana abul kalam | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5436
1037 | Moulana abul kalam | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5437
1038 | Moulana abul kalam | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5438
1039 | Moulana abul kalam | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5439
1040 | Moulana abul kalam | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5440
1041 | Moulana abul kalam | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5441
1042 | Moulana abul kalam | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5442
1043 | Moulana abul kalam | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5443
1044 | Moulana abul kalam | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5444
1045 | K Feeder | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 455
1046 | K Feeder | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 456
1047 | K Feeder | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 457
1048 | K Feeder | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 458
1049 | K Feeder | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 459
1050 | K Feeder | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 460
1051 | K Feeder | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 461
1052 | K Feeder | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 462
1053 | K Feeder | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 463
1054 | K Feeder | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 464
1055 | K Feeder | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 465
1056 | K Feeder | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 466
1057 | K Feeder | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 467
1058 | K Feeder | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 468
1059 | K Feeder | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10028
1060 | K Feeder | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10028
1061 | K Feeder | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1062 | K Feeder | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1063 | K Feeder | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13089
1064 | K Feeder | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5445
1065 | K Feeder | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5446
1066 | K Feeder | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5447
1067 | K Feeder | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5448
1068 | K Feeder | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5449
1069 | K Feeder | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5450
1070 | K Feeder | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5451
1071 | K Feeder | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5452
1072 | K Feeder | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5453
1073 | K Feeder | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5454
1074 | K Feeder | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5455
1075 | K Feeder | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5456
1076 | K Feeder | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5457
1077 | K Feeder | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5458
1078 | K Feeder | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5459
1079 | K Feeder | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5460
1080 | K Feeder | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5461
1081 | Tr-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 469
1082 | Tr-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 470
1083 | Tr-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 471
1084 | Tr-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 472
1085 | Tr-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 473
1086 | Tr-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 474
1087 | Tr-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 475
1088 | Tr-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 476
1089 | Tr-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 477
1090 | Tr-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 478
1091 | Tr-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 479
1092 | Tr-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 480
1093 | Tr-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 481
1094 | Tr-2 | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10029
1095 | Tr-2 | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10029
1096 | Tr-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1097 | Tr-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1098 | Tr-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13092
1099 | Tr-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5462
1100 | Tr-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5463
1101 | Tr-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5464
1102 | Tr-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5465
1103 | Tr-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5466
1104 | Tr-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5467
1105 | Tr-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5468
1106 | Tr-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5469
1107 | Tr-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5470
1108 | Tr-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5471
1109 | Tr-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5472
1110 | Tr-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5473
1111 | Tr-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5474
1112 | Tr-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5475
1113 | Tr-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5476
1114 | Tr-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5477
1115 | Tr-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5478
1116 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 482
1117 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 483
1118 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 484
1119 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 485
1120 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 486
1121 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 487
1122 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 488
1123 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 489 |  |  |  | AC CMR to be used
1124 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 490
1125 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 491
1126 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close Command | DPC |  |  | Hard | HDR | 10030
1127 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open Command | DPC |  |  | Hard | HDR | 10030
1128 | M3 M2 Inter connector | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 492
1129 | M3 M2 Inter connector | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 493
1130 | M3 M2 Inter connector | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 494
1131 | M3 M2 Inter connector | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 495
1132 | M3 M2 Inter connector | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 496
1133 | M3 M2 Inter connector | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 497
1134 | M3 M2 Inter connector | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 498
1135 | M3 M2 Inter connector | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 499
1136 | M3 M2 Inter connector | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 500
1137 | M3 M2 Inter connector | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 501
1138 | M3 M2 Inter connector | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 502
1139 | M3 M2 Inter connector | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 503
1140 | M3 M2 Inter connector | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 504
1141 | M3 M2 Inter connector | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10031
1142 | M3 M2 Inter connector | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10031
1143 | M3 M2 Inter connector | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13093
1144 | M3 M2 Inter connector | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13094
1145 | M3 M2 Inter connector | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13095
1146 | M3 M2 Inter connector | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5479
1147 | M3 M2 Inter connector | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5480
1148 | M3 M2 Inter connector | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5481
1149 | M3 M2 Inter connector | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5482
1150 | M3 M2 Inter connector | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5483
1151 | M3 M2 Inter connector | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5484
1152 | M3 M2 Inter connector | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5485
1153 | M3 M2 Inter connector | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5486
1154 | M3 M2 Inter connector | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5487
1155 | M3 M2 Inter connector | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5488
1156 | M3 M2 Inter connector | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5489
1157 | M3 M2 Inter connector | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5490
1158 | M3 M2 Inter connector | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5491
1159 | M3 M2 Inter connector | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5492
1160 | M3 M2 Inter connector | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5493
1161 | M3 M2 Inter connector | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5494
1162 | M3 M2 Inter connector | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5495
1163 | T STD T1 Inter connector | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 505
1164 | T STD T1 Inter connector | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 506
1165 | T STD T1 Inter connector | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 507
1166 | T STD T1 Inter connector | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 508
1167 | T STD T1 Inter connector | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 509
1168 | T STD T1 Inter connector | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 510
1169 | T STD T1 Inter connector | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 511
1170 | T STD T1 Inter connector | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 512
1171 | T STD T1 Inter connector | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 513
1172 | T STD T1 Inter connector | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 514
1173 | T STD T1 Inter connector | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 515
1174 | T STD T1 Inter connector | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 516
1175 | T STD T1 Inter connector | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 517
1176 | T STD T1 Inter connector | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10032
1177 | T STD T1 Inter connector | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10032
1178 | T STD T1 Inter connector | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13096
1179 | T STD T1 Inter connector | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13097
1180 | T STD T1 Inter connector | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13098
1181 | T STD T1 Inter connector | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5496
1182 | T STD T1 Inter connector | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5497
1183 | T STD T1 Inter connector | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5498
1184 | T STD T1 Inter connector | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5499
1185 | T STD T1 Inter connector | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5500
1186 | T STD T1 Inter connector | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5501
1187 | T STD T1 Inter connector | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5502
1188 | T STD T1 Inter connector | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5503
1189 | T STD T1 Inter connector | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5504
1190 | T STD T1 Inter connector | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5505
1191 | T STD T1 Inter connector | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5506
1192 | T STD T1 Inter connector | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5507
1193 | T STD T1 Inter connector | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5508
1194 | T STD T1 Inter connector | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5509
1195 | T STD T1 Inter connector | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5510
1196 | T STD T1 Inter connector | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5511
1197 | T STD T1 Inter connector | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5512
1198 | Hygiene\Tata | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 518
1199 | Hygiene\Tata | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 519
1200 | Hygiene\Tata | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 520
1201 | Hygiene\Tata | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 521
1202 | Hygiene\Tata | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 522
1203 | Hygiene\Tata | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 523
1204 | Hygiene\Tata | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 524
1205 | Hygiene\Tata | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 525
1206 | Hygiene\Tata | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 526
1207 | Hygiene\Tata | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 527
1208 | Hygiene\Tata | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 528
1209 | Hygiene\Tata | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 529
1210 | Hygiene\Tata | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 530
1211 | Hygiene\Tata | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 531
1212 | Hygiene\Tata | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10033
1213 | Hygiene\Tata | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10033
1214 | Hygiene\Tata | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13099
1215 | Hygiene\Tata | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13100
1216 | Hygiene\Tata | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13101
1217 | Hygiene\Tata | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5513
1218 | Hygiene\Tata | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5514
1219 | Hygiene\Tata | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5515
1220 | Hygiene\Tata | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5516
1221 | Hygiene\Tata | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5517
1222 | Hygiene\Tata | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5518
1223 | Hygiene\Tata | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5519
1224 | Hygiene\Tata | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5520
1225 | Hygiene\Tata | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5521
1226 | Hygiene\Tata | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5522
1227 | Hygiene\Tata | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5523
1228 | Hygiene\Tata | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5524
1229 | Hygiene\Tata | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5525
1230 | Hygiene\Tata | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5526
1231 | Hygiene\Tata | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5527
1232 | Hygiene\Tata | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5528
1233 | Hygiene\Tata | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5529
1234 | J Feeder | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 532
1235 | J Feeder | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 533
1236 | J Feeder | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 534
1237 | J Feeder | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 535
1238 | J Feeder | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 536
1239 | J Feeder | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 537
1240 | J Feeder | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 538
1241 | J Feeder | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 539
1242 | J Feeder | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 540
1243 | J Feeder | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 541
1244 | J Feeder | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 542
1245 | J Feeder | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 543
1246 | J Feeder | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 544
1247 | J Feeder | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 545
1248 | J Feeder | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10034
1249 | J Feeder | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10034
1250 | J Feeder | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13102
1251 | J Feeder | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13103
1252 | J Feeder | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13104
1253 | J Feeder | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5530
1254 | J Feeder | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5531
1255 | J Feeder | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5532
1256 | J Feeder | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5533
1257 | J Feeder | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5534
1258 | J Feeder | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5535
1259 | J Feeder | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5536
1260 | J Feeder | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5537
1261 | J Feeder | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5538
1262 | J Feeder | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5539
1263 | J Feeder | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5540
1264 | J Feeder | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5541
1265 | J Feeder | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5542
1266 | J Feeder | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5543
1267 | J Feeder | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5544
1268 | J Feeder | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5545
1269 | J Feeder | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5546
1270 | Tr-5 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 546
1271 | Tr-5 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 547
1272 | Tr-5 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 548
1273 | Tr-5 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 549
1274 | Tr-5 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 550
1275 | Tr-5 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 551
1276 | Tr-5 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 552
1277 | Tr-5 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 553
1278 | Tr-5 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 554
1279 | Tr-5 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 555
1280 | Tr-5 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 556
1281 | Tr-5 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 557
1282 | Tr-5 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 558
1283 | Tr-5 | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10035
1284 | Tr-5 | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10035
1285 | Tr-5 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13105
1286 | Tr-5 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13106
1287 | Tr-5 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13107
1288 | Tr-5 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5547
1289 | Tr-5 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5548
1290 | Tr-5 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5549
1291 | Tr-5 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5550
1292 | Tr-5 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5551
1293 | Tr-5 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5552
1294 | Tr-5 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5553
1295 | Tr-5 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5554
1296 | Tr-5 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5555
1297 | Tr-5 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5556
1298 | Tr-5 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5557
1299 | Tr-5 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5558
1300 | Tr-5 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5559
1301 | Tr-5 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5560
1302 | Tr-5 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5561
1303 | Tr-5 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5562
1304 | Tr-5 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5563
1305 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 559
1306 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 560
1307 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 561
1308 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 562
1309 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 563
1310 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 564
1311 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 565
1312 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 566
1313 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 567
1314 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 568
1315 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 569
1316 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 570
1317 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 571
1318 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 572
1319 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10036
1320 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10036
1321 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13108
1322 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13109
1323 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13110
1324 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5564
1325 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5565
1326 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5566
1327 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5567
1328 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5568
1329 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5569
1330 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5570
1331 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5571
1332 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5572
1333 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5573
1334 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5574
1335 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5575
1336 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5576
1337 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5577
1338 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5578
1339 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5579
1340 | M3 Outdoor RMU & Nicco park | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5580
1341 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 573
1342 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 574
1343 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 575
1344 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 576
1345 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 577
1346 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 578
1347 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 579
1348 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 580
1349 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 581
1350 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 582
1351 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 583
1352 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 584
1353 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 585
1354 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10037
1355 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10037
1356 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13111
1357 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13112
1358 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13113
1359 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5581
1360 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5582
1361 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5583
1362 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5584
1363 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5585
1364 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5586
1365 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5587
1366 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5588
1367 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5589
1368 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5590
1369 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5591
1370 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5592
1371 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5593
1372 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5594
1373 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5595
1374 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5596
1375 | Inter Connector Tr1-Tr Stadium | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5597
1376 | Stadium fdr-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 586
1377 | Stadium fdr-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 587
1378 | Stadium fdr-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 588
1379 | Stadium fdr-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 589
1380 | Stadium fdr-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 590
1381 | Stadium fdr-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 591
1382 | Stadium fdr-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 592
1383 | Stadium fdr-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 593
1384 | Stadium fdr-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 594
1385 | Stadium fdr-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 595
1386 | Stadium fdr-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 596
1387 | Stadium fdr-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 597
1388 | Stadium fdr-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 598
1389 | Stadium fdr-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 599
1390 | Stadium fdr-2 | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10038
1391 | Stadium fdr-2 | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10038
1392 | Stadium fdr-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13114
1393 | Stadium fdr-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13115
1394 | Stadium fdr-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13116
1395 | Stadium fdr-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5598
1396 | Stadium fdr-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5599
1397 | Stadium fdr-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5600
1398 | Stadium fdr-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5601
1399 | Stadium fdr-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5602
1400 | Stadium fdr-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5603
1401 | Stadium fdr-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5604
1402 | Stadium fdr-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5605
1403 | Stadium fdr-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5606
1404 | Stadium fdr-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5607
1405 | Stadium fdr-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5608
1406 | Stadium fdr-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5609
1407 | Stadium fdr-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5610
1408 | Stadium fdr-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5611
1409 | Stadium fdr-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5612
1410 | Stadium fdr-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5613
1411 | Stadium fdr-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5614
1412 | Stadium fdr-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 600
1413 | Stadium fdr-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 601
1414 | Stadium fdr-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 602
1415 | Stadium fdr-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 603
1416 | Stadium fdr-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 604
1417 | Stadium fdr-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 605
1418 | Stadium fdr-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 606
1419 | Stadium fdr-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 607
1420 | Stadium fdr-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 608
1421 | Stadium fdr-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 609
1422 | Stadium fdr-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 610
1423 | Stadium fdr-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 611
1424 | Stadium fdr-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 612
1425 | Stadium fdr-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 613
1426 | Stadium fdr-1 | 11kV | Outgoing | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10039
1427 | Stadium fdr-1 | 11kV | Outgoing | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10039
1428 | Stadium fdr-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13117
1429 | Stadium fdr-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13118
1430 | Stadium fdr-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13119
1431 | Stadium fdr-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5615
1432 | Stadium fdr-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5616
1433 | Stadium fdr-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5617
1434 | Stadium fdr-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5618
1435 | Stadium fdr-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5619
1436 | Stadium fdr-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5620
1437 | Stadium fdr-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5621
1438 | Stadium fdr-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5622
1439 | Stadium fdr-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5623
1440 | Stadium fdr-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5624
1441 | Stadium fdr-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5625
1442 | Stadium fdr-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5626
1443 | Stadium fdr-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5627
1444 | Stadium fdr-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5628
1445 | Stadium fdr-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5629
1446 | Stadium fdr-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5630
1447 | Stadium fdr-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5631
1448 | Tr Stadium | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 614
1449 | Tr Stadium | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 615
1450 | Tr Stadium | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 616
1451 | Tr Stadium | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 617
1452 | Tr Stadium | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 618
1453 | Tr Stadium | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 619
1454 | Tr Stadium | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 620
1455 | Tr Stadium | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 621
1456 | Tr Stadium | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 622
1457 | Tr Stadium | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 623
1458 | Tr Stadium | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 624
1459 | Tr Stadium | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 625
1460 | Tr Stadium | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 626
1461 | Tr Stadium | 11kV | Incomer | Circuit Breaker Close Command | DPC |  |  | Soft | IED | 10040
1462 | Tr Stadium | 11kV | Incomer | Circuit Breaker Open Command | DPC |  |  | Soft | IED | 10040
1463 | Tr Stadium | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13120
1464 | Tr Stadium | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13121
1465 | Tr Stadium | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13122
1466 | Tr Stadium | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5632
1467 | Tr Stadium | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5633
1468 | Tr Stadium | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5634
1469 | Tr Stadium | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5635
1470 | Tr Stadium | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5636
1471 | Tr Stadium | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5637
1472 | Tr Stadium | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5638
1473 | Tr Stadium | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5639
1474 | Tr Stadium | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5640
1475 | Tr Stadium | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5641
1476 | Tr Stadium | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5642
1477 | Tr Stadium | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5643
1478 | Tr Stadium | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5644
1479 | Tr Stadium | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5645
1480 | Tr Stadium | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5646
1481 | Tr Stadium | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5647
1482 | Tr Stadium | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5648
1483 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5649
1484 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5650
1485 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5651
1486 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5652
1487 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5653
1488 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5654
1489 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5655