## Signal List
SCADA/Advanced Distribution Management System (ADMS)
S.No. | Feeder Name | Voltage Level | Feeder Type | Signal Description | Signal Type | Unit | Input Range | Hard/Soft | Source | IEC-104 Mapping Add. | IEC61850/RS485 | Local Validation | End To End Validation | Remark
1 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Under Voltage | SPI |  |  | Hard | CMR | 1
2 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger Over Voltage | SPI |  |  | Hard | CMR | 2
3 | 48V DCPS | 48V | DC DIST. BOARD | 48V DC Charger AC Supply Fail | SPI |  |  | Hard | CMR | 3 |  |  |  | AC CMR to be used
4 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Voltage | AI |  |  | Hard | Transducer | 5000
5 | 48V DCPS | 48V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5001
6 | 30V DC1 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 4 |  |  |  | AC CMR to be used
7 | 30V DC1 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 5
8 | 30V DC1 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 6
9 | 30V DC1 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 7
10 | 30V DC1 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 8
11 | 30V DC1 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5002
12 | 30V DC1 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5003
13 | 30V DC1 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5004
14 | 30V DC2 | 30V | DC DIST. BOARD | AC Supply Fail | SPI |  |  | Hard | CMR | 9 |  |  |  | AC CMR to be used
15 | 30V DC2 | 30V | DC DIST. BOARD | DC Low voltage | SPI |  |  | Hard | CMR | 10
16 | 30V DC2 | 30V | DC DIST. BOARD | AC Low voltage | SPI |  |  | Hard | CMR | 11
17 | 30V DC2 | 30V | DC DIST. BOARD | DC System E/F | SPI |  |  | Hard | CMR | 12
18 | 30V DC2 | 30V | DC DIST. BOARD | Battery On Boost | SPI |  |  | Hard | CMR | 13
19 | 30V DC2 | 30V | DC DIST. BOARD | DC load Voltage | AI |  | 0-30V DC | Hard | Transducer | 5005
20 | 30V DC2 | 30V | DC DIST. BOARD | DC Load Current | AI |  |  | Hard | Transducer | 5006
21 | 30V DC2 | 30V | DC DIST. BOARD | Battery Current | AI |  |  | Hard | Transducer | 5007
22 | Sub-Station Common |  | Common | Dummy CB Open/Close | DPI |  |  | Hard | DUMMY CB | 3000
23 | Sub-Station Common |  | Common | Dummy Open/Close Command | DPC |  |  | Hard | DUMMY CB | 10000
24 | Sub-Station Common |  | Common | RTU L/R Status | DPI |  |  | Hard | L/R Switch | 3001
25 | Sub-Station Common |  | Common | RTU Panel Power Supply Fail | SPI |  |  | Hard | CMR | 14 |  |  |  | AC CMR to be used
26 | Sub-Station Common |  | Common | RTU Communication Status | SPI |  |  | Soft | RTU | 15
27 | Sub-Station Common |  | Common | RTU door Status | DPI |  |  | Hard | RTU | 3002
28 | Transformer-1 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 16
29 | Transformer-1 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 17
30 | Transformer-1 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 18
31 | Transformer-1 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 19
32 | Transformer-1 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 20
33 | Transformer-1 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 21
34 | Transformer-1 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 22
35 | Transformer-1 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 23
36 | Transformer-1 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 24
37 | Transformer-1 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 25
38 | Transformer-1 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 26
39 | Transformer-1 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 27
40 | Transformer-1 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 28
41 | Transformer-1 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 29
42 | Transformer-1 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 30
43 | Transformer-1 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 31
44 | Transformer-1 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 32
45 | Transformer-1 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 33
46 | Transformer-1 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 34
47 | Transformer-1 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 35
48 | Transformer-1 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 36
49 | Transformer-1 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 37
50 | Transformer-1 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 38
51 | Transformer-1 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 39
52 | Transformer-1 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13000
53 | Transformer-1 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13001
54 | Transformer-1 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13002
55 | Transformer-1 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13003
56 | Transformer-1 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10001
57 | Transformer-1 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10001
58 | Transformer-1 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5008
59 | Transformer-1 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5009
60 | Transformer-1 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5010
61 | Transformer-1 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5011
62 | Transformer-1 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5012
63 | Transformer-1 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5013
64 | Transformer-1 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5014
65 | Transformer-1 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5015
66 | Transformer-1 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5016
67 | Transformer-1 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5017
68 | Transformer-1 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5018
69 | Transformer-1 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5019
70 | Transformer-1 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5020
71 | Transformer-1 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5021
72 | Transformer-1 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5022
73 | Transformer-1 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5023
74 | Transformer-1 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5024
75 | Transformer-1 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 40
76 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 41
77 | Transformer-1 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 42 |  |  |  | AC CMR to be used
78 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 43
79 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 44
80 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 45
81 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 46
82 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 47
83 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13004
84 | Transformer-1 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13005
85 | Transformer-1 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5025
86 | Transformer-1 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5026
87 | Transformer-1 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5027
88 | Transformer-2 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 48
89 | Transformer-2 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 49
90 | Transformer-2 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 50
91 | Transformer-2 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 51
92 | Transformer-2 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 52
93 | Transformer-2 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 53
94 | Transformer-2 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 54
95 | Transformer-2 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 55
96 | Transformer-2 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 56
97 | Transformer-2 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 57
98 | Transformer-2 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 58
99 | Transformer-2 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 59
100 | Transformer-2 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 60
101 | Transformer-2 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 61
102 | Transformer-2 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 62
103 | Transformer-2 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 63
104 | Transformer-2 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 64
105 | Transformer-2 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 65
106 | Transformer-2 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 66
107 | Transformer-2 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 67
108 | Transformer-2 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 68
109 | Transformer-2 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 69
110 | Transformer-2 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 70
111 | Transformer-2 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 71
112 | Transformer-2 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13006
113 | Transformer-2 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13007
114 | Transformer-2 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13008
115 | Transformer-2 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13009
116 | Transformer-2 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10002
117 | Transformer-2 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10002
118 | Transformer-2 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5028
119 | Transformer-2 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5029
120 | Transformer-2 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5030
121 | Transformer-2 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5031
122 | Transformer-2 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5032
123 | Transformer-2 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5033
124 | Transformer-2 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5034
125 | Transformer-2 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5035
126 | Transformer-2 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5036
127 | Transformer-2 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5037
128 | Transformer-2 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5038
129 | Transformer-2 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5039
130 | Transformer-2 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5040
131 | Transformer-2 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5041
132 | Transformer-2 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5042
133 | Transformer-2 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5043
134 | Transformer-2 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5044
135 | Transformer-2 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 72
136 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 73
137 | Transformer-2 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 74 |  |  |  | AC CMR to be used
138 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 75
139 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 76
140 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 77
141 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 78
142 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 79
143 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13010
144 | Transformer-2 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13011
145 | Transformer-2 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5045
146 | Transformer-2 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5046
147 | Transformer-2 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5047
148 | Transformer-3 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 80
149 | Transformer-3 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 81
150 | Transformer-3 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 82
151 | Transformer-3 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 83
152 | Transformer-3 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 84
153 | Transformer-3 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 85
154 | Transformer-3 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 86
155 | Transformer-3 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 87
156 | Transformer-3 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 88
157 | Transformer-3 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 89
158 | Transformer-3 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 90
159 | Transformer-3 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 91
160 | Transformer-3 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 92
161 | Transformer-3 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 93
162 | Transformer-3 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 94
163 | Transformer-3 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 95
164 | Transformer-3 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 96
165 | Transformer-3 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 97
166 | Transformer-3 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 98
167 | Transformer-3 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 99
168 | Transformer-3 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 100
169 | Transformer-3 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 101
170 | Transformer-3 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 102
171 | Transformer-3 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 103
172 | Transformer-3 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13012
173 | Transformer-3 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13013
174 | Transformer-3 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13014
175 | Transformer-3 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13015
176 | Transformer-3 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10003
177 | Transformer-3 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10003
178 | Transformer-3 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5048
179 | Transformer-3 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5049
180 | Transformer-3 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5050
181 | Transformer-3 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5051
182 | Transformer-3 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5052
183 | Transformer-3 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5053
184 | Transformer-3 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5054
185 | Transformer-3 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5055
186 | Transformer-3 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5056
187 | Transformer-3 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5057
188 | Transformer-3 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5058
189 | Transformer-3 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5059
190 | Transformer-3 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5060
191 | Transformer-3 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5061
192 | Transformer-3 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5062
193 | Transformer-3 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5063
194 | Transformer-3 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5064
195 | Transformer-3 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 104
196 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 105
197 | Transformer-3 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 106 |  |  |  | AC CMR to be used
198 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 107
199 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 108
200 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 109
201 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 110
202 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 111
203 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13016
204 | Transformer-3 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13017
205 | Transformer-3 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5065
206 | Transformer-3 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5066
207 | Transformer-3 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5067
208 | Transformer-4 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 112
209 | Transformer-4 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 113
210 | Transformer-4 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 114
211 | Transformer-4 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 115
212 | Transformer-4 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 116
213 | Transformer-4 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 117
214 | Transformer-4 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 118
215 | Transformer-4 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 119
216 | Transformer-4 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 120
217 | Transformer-4 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 121
218 | Transformer-4 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 122
219 | Transformer-4 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 123
220 | Transformer-4 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 124
221 | Transformer-4 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 125
222 | Transformer-4 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 126
223 | Transformer-4 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 127
224 | Transformer-4 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 128
225 | Transformer-4 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 129
226 | Transformer-4 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 130
227 | Transformer-4 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 131
228 | Transformer-4 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 132
229 | Transformer-4 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 133
230 | Transformer-4 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 134
231 | Transformer-4 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 135
232 | Transformer-4 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13018
233 | Transformer-4 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13019
234 | Transformer-4 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13020
235 | Transformer-4 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13021
236 | Transformer-4 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10004
237 | Transformer-4 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10004
238 | Transformer-4 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5068
239 | Transformer-4 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5069
240 | Transformer-4 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5070
241 | Transformer-4 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5071
242 | Transformer-4 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5072
243 | Transformer-4 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5073
244 | Transformer-4 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5074
245 | Transformer-4 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5075
246 | Transformer-4 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5076
247 | Transformer-4 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5077
248 | Transformer-4 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5078
249 | Transformer-4 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5079
250 | Transformer-4 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5080
251 | Transformer-4 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5081
252 | Transformer-4 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5082
253 | Transformer-4 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5083
254 | Transformer-4 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5084
255 | Transformer-4 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 136
256 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 137
257 | Transformer-4 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 138 |  |  |  | AC CMR to be used
258 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 139
259 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 140
260 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 141
261 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 142
262 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 143
263 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13022
264 | Transformer-4 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13023
265 | Transformer-4 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5085
266 | Transformer-4 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5086
267 | Transformer-4 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5087
268 | Transformer-5 | 33kV | Transformer | Circuit Breaker Close | SPI |  |  | Soft | IED1 | 144
269 | Transformer-5 | 33kV | Transformer | Circuit Breaker Open | SPI |  |  | Soft | IED1 | 145
270 | Transformer-5 | 33kV | Transformer | Auto Trip | SPI |  |  | Soft | IED1 | 146
271 | Transformer-5 | 33kV | Transformer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED1 | 147
272 | Transformer-5 | 33kV | Transformer | Spring Charged | SPI |  |  | Soft | IED1 | 148
273 | Transformer-5 | 33kV | Transformer | Earth Fault Operated | SPI |  |  | Soft | IED1 | 149
274 | Transformer-5 | 33kV | Transformer | Over Current Operated | SPI |  |  | Soft | IED1 | 150
275 | Transformer-5 | 33kV | Transformer | Differential Operated | SPI |  |  | Soft | IED2 | 151
276 | Transformer-5 | 33kV | Transformer | Master Trip Relay Operated(MTR) | SPI |  |  | Soft | IED1 | 152
277 | Transformer-5 | 33kV | Transformer | OSR Trip | SPI |  |  | Hard | CMR | 153
278 | Transformer-5 | 33kV | Transformer | PRV Trip/OLTC PRV | SPI |  |  | Hard | CMR | 154
279 | Transformer-5 | 33kV | Transformer | OTI Alarm | SPI |  |  | Hard | CMR | 155
280 | Transformer-5 | 33kV | Transformer | OTI Trip | SPI |  |  | Hard | CMR | 156
281 | Transformer-5 | 33kV | Transformer | WTI Alarm | SPI |  |  | Hard | CMR | 157
282 | Transformer-5 | 33kV | Transformer | WTI Trip | SPI |  |  | Hard | CMR | 158
283 | Transformer-5 | 33kV | Transformer | Buccholz Alarm | SPI |  |  | Hard | CMR | 159
284 | Transformer-5 | 33kV | Transformer | Buccholz Trip | SPI |  |  | Hard | CMR | 160
285 | Transformer-5 | 33kV | Transformer | Oil Level Low (MOG Alarm) | SPI |  |  | Hard | CMR | 161
286 | Transformer-5 | 33kV | Transformer | IRF of IED1 | SPI |  |  | Hard | CMR | 162
287 | Transformer-5 | 33kV | Transformer | IRF of IED2 | SPI |  |  | Hard | CMR | 163
288 | Transformer-5 | 33kV | Transformer | REF Protection HV Side | SPI |  |  | Soft | IED2 | 164
289 | Transformer-5 | 33kV | Transformer | REF Protection LV Side | SPI |  |  | Soft | IED2 | 165
290 | Transformer-5 | 33kV | Transformer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 166
291 | Transformer-5 | 33kV | Transformer | C/R Panel Remote Position | SPI |  |  | Soft | IED1 | 167
292 | Transformer-5 | 33kV | Transformer | Master Trip Relay Reset (MTR) + Annunciator Accept | SPC |  |  | Hard | HDR | 13024
293 | Transformer-5 | 33kV | Transformer | Annunciator Reset | SPC |  |  | Hard | HDR | 13025
294 | Transformer-5 | 33kV | Transformer | IED1 Reset | SPC |  |  | Soft | IED1 | 13026
295 | Transformer-5 | 33kV | Transformer | IED2 Reset | SPC |  |  | Soft | IED2 | 13027
296 | Transformer-5 | 33kV | Transformer | Circuit breaker Close Command | DPC |  |  | Soft | IED1 | 10005
297 | Transformer-5 | 33kV | Transformer | Circuit breaker Open Command | DPC |  |  | Soft | IED1 | 10005
298 | Transformer-5 | 33kV | Transformer | Voltage RY | AI |  | 110V AC | Soft | MFT | 5088
299 | Transformer-5 | 33kV | Transformer | Voltage YB | AI |  | 110V AC | Soft | MFT | 5089
300 | Transformer-5 | 33kV | Transformer | Voltage BR | AI |  | 110V AC | Soft | MFT | 5090
301 | Transformer-5 | 33kV | Transformer | Current R Phase | AI |  | 1/5 A | Soft | MFT | 5091
302 | Transformer-5 | 33kV | Transformer | Current Y Phase | AI |  | 1/5 A | Soft | MFT | 5092
303 | Transformer-5 | 33kV | Transformer | Unbalance Current | AI |  | 1/5 A | Soft | MFT | 5093
304 | Transformer-5 | 33kV | Transformer | Current B Phase | AI |  | 1/5 A | Soft | MFT | 5094
305 | Transformer-5 | 33kV | Transformer | Active Power | AI |  |  | Soft | MFT | 5095
306 | Transformer-5 | 33kV | Transformer | Reactive Power | AI |  |  | Soft | MFT | 5096
307 | Transformer-5 | 33kV | Transformer | Power Factor | AI |  |  | Soft | MFT | 5097
308 | Transformer-5 | 33kV | Transformer | Phase Angle RY | AI |  |  | Soft | MFT | 5098
309 | Transformer-5 | 33kV | Transformer | Phase Angle YB | AI |  |  | Soft | MFT | 5099
310 | Transformer-5 | 33kV | Transformer | Phase Angle BR | AI |  |  | Soft | MFT | 5100
311 | Transformer-5 | 33kV | Transformer | Active Energy Import | AI |  |  | Soft | MFT | 5101
312 | Transformer-5 | 33kV | Transformer | Active Energy Export | AI |  |  | Soft | MFT | 5102
313 | Transformer-5 | 33kV | Transformer | Reactive Energy Import | AI |  |  | Soft | MFT | 5103
314 | Transformer-5 | 33kV | Transformer | Reactive Energy Export | AI |  |  | Soft | MFT | 5104
315 | Transformer-5 (RTCC) | 33kV | Transformer | Out Of Step | SPI |  |  | Hard | CMR | 168
316 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Control Supply Fail | SPI |  |  | Hard | CMR | 169
317 | Transformer-5 (RTCC) | 33kV | Transformer | Motor Supply Fail | SPI |  |  | Hard | CMR | 170 |  |  |  | AC CMR to be used
318 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer On SCADA | SPI |  |  | Hard | CMR | 171
319 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer On Local | SPI |  |  | Hard | CMR | 172
320 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Master | SPI |  |  | Hard | CMR | 173
321 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Follower | SPI |  |  | Hard | CMR | 174
322 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Changer Individual | SPI |  |  | Hard | CMR | 175
323 | Transformer-5 (RTCC) | 33kV | Transformer | Tap-changer Raise command | SPC |  |  | Hard | HDR | 13028
324 | Transformer-5 (RTCC) | 33kV | Transformer | Tap-changer Lower command | SPC |  |  | Hard | HDR | 13029
325 | Transformer-5 (RTCC) | 33kV | Transformer | Tap Position | AI |  | 0-17K ohm | Hard | Transducer | 5105
326 | Transformer-5 (RTCC) | 33kV | Transformer | WindingTemperature | AI |  | 0-150'C | Hard | Transducer | 5106
327 | Transformer-5 (RTCC) | 33kV | Transformer | Oil Temperature | AI |  | 0-150'C | Hard | Transducer | 5107
328 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 176
329 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 177
330 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 178
331 | M5-M3 Inter connector | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 179
332 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 180
333 | M5-M3 Inter connector | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 181
334 | M5-M3 Inter connector | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 182
335 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 183
336 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 184
337 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 185
338 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 186
339 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 187
340 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13030
341 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13031
342 | M5-M3 Inter connector | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13032
343 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10006
344 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10006
345 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5108
346 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5109
347 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5110
348 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5111
349 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5112
350 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5113
351 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5114
352 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5115
353 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5116
354 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5117
355 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5118
356 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5119
357 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5120
358 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5121
359 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5122
360 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5123
361 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5124
362 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5125
363 | M5-M3 Inter connector | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5126
364 | Wipro fdr | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 188
365 | Wipro fdr | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 189
366 | Wipro fdr | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 190
367 | Wipro fdr | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 191
368 | Wipro fdr | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 192
369 | Wipro fdr | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 193
370 | Wipro fdr | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 194
371 | Wipro fdr | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 195
372 | Wipro fdr | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 196
373 | Wipro fdr | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 197
374 | Wipro fdr | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 198
375 | Wipro fdr | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 199
376 | Wipro fdr | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13033
377 | Wipro fdr | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13034
378 | Wipro fdr | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13035
379 | Wipro fdr | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10007
380 | Wipro fdr | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10007
381 | Wipro fdr | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5127
382 | Wipro fdr | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5128
383 | Wipro fdr | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5129
384 | Wipro fdr | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5130
385 | Wipro fdr | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5131
386 | Wipro fdr | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5132
387 | Wipro fdr | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5133
388 | Wipro fdr | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5134
389 | Wipro fdr | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5135
390 | Wipro fdr | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5136
391 | Wipro fdr | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5137
392 | Wipro fdr | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5138
393 | Wipro fdr | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5139
394 | Wipro fdr | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5140
395 | Wipro fdr | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5141
396 | Wipro fdr | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5142
397 | Wipro fdr | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5143
398 | Wipro fdr | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5144
399 | Wipro fdr | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5145
400 | Salt lake M V incomer fdr-I | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 200
401 | Salt lake M V incomer fdr-I | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 201
402 | Salt lake M V incomer fdr-I | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 202
403 | Salt lake M V incomer fdr-I | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 203
404 | Salt lake M V incomer fdr-I | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 204
405 | Salt lake M V incomer fdr-I | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 205
406 | Salt lake M V incomer fdr-I | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 206
407 | Salt lake M V incomer fdr-I | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 207
408 | Salt lake M V incomer fdr-I | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 208
409 | Salt lake M V incomer fdr-I | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 209
410 | Salt lake M V incomer fdr-I | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 210
411 | Salt lake M V incomer fdr-I | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 211
412 | Salt lake M V incomer fdr-I | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13036
413 | Salt lake M V incomer fdr-I | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13037
414 | Salt lake M V incomer fdr-I | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13038
415 | Salt lake M V incomer fdr-I | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10008
416 | Salt lake M V incomer fdr-I | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10008
417 | Salt lake M V incomer fdr-I | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5146
418 | Salt lake M V incomer fdr-I | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5147
419 | Salt lake M V incomer fdr-I | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5148
420 | Salt lake M V incomer fdr-I | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5149
421 | Salt lake M V incomer fdr-I | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5150
422 | Salt lake M V incomer fdr-I | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5151
423 | Salt lake M V incomer fdr-I | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5152
424 | Salt lake M V incomer fdr-I | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5153
425 | Salt lake M V incomer fdr-I | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5154
426 | Salt lake M V incomer fdr-I | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5155
427 | Salt lake M V incomer fdr-I | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5156
428 | Salt lake M V incomer fdr-I | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5157
429 | Salt lake M V incomer fdr-I | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5158
430 | Salt lake M V incomer fdr-I | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5159
431 | Salt lake M V incomer fdr-I | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5160
432 | Salt lake M V incomer fdr-I | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5161
433 | Salt lake M V incomer fdr-I | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5162
434 | Salt lake M V incomer fdr-I | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5163
435 | Salt lake M V incomer fdr-I | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5164
436 | ABP fdr | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 212
437 | ABP fdr | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 213
438 | ABP fdr | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 214
439 | ABP fdr | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 215
440 | ABP fdr | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 216
441 | ABP fdr | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 217
442 | ABP fdr | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 218
443 | ABP fdr | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 219
444 | ABP fdr | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 220
445 | ABP fdr | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 221
446 | ABP fdr | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 222
447 | ABP fdr | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 223
448 | ABP fdr | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13039
449 | ABP fdr | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13040
450 | ABP fdr | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13041
451 | ABP fdr | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10009
452 | ABP fdr | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10009
453 | ABP fdr | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5165
454 | ABP fdr | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5166
455 | ABP fdr | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5167
456 | ABP fdr | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5168
457 | ABP fdr | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5169
458 | ABP fdr | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5170
459 | ABP fdr | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5171
460 | ABP fdr | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5172
461 | ABP fdr | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5173
462 | ABP fdr | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5174
463 | ABP fdr | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5175
464 | ABP fdr | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5176
465 | ABP fdr | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5177
466 | ABP fdr | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5178
467 | ABP fdr | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5179
468 | ABP fdr | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5180
469 | ABP fdr | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5181
470 | ABP fdr | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5182
471 | ABP fdr | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5183
472 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 224
473 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 225
474 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 226
475 | Salt lake M V Incomer fdr-II | 33kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 227
476 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 228
477 | Salt lake M V Incomer fdr-II | 33kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 229
478 | Salt lake M V Incomer fdr-II | 33kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 230
479 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 231
480 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 232
481 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Broken conductor optd | SPI |  |  | Soft | IED | 233
482 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 234
483 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 235
484 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13042
485 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13043
486 | Salt lake M V Incomer fdr-II | 33kV | Incomer | IED RESET | SPC |  |  | Soft | IED | 13044
487 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10010
488 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10010
489 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5184
490 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5185
491 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5186
492 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5187
493 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5188
494 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5189
495 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5190
496 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5191
497 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5192
498 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5193
499 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5194
500 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5195
501 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5196
502 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5197
503 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5198
504 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5199
505 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5200
506 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Bus Voltage | AI |  |  | Soft | MFT | 5201
507 | Salt lake M V Incomer fdr-II | 33kV | Incomer | Bus Frequency | AI |  |  | Soft | MFT | 5202
508 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 236
509 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 237
510 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Auto Trip | SPI |  |  | Soft | IED | 238
511 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 239
512 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Spring Charged | SPI |  |  | Soft | IED | 240
513 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 241
514 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 242
515 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 243
516 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 244
517 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 245
518 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 246
519 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 247
520 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13045
521 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13046
522 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | IED RESET | SPC |  |  | Soft | IED | 13047
523 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10011
524 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10011
525 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5203
526 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5204
527 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5205
528 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5206
529 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5207
530 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5208
531 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Active Power | AI |  |  | Soft | MFT | 5209
532 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5210
533 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Power Factor | AI |  |  | Soft | MFT | 5211
534 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5212
535 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5213
536 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5214
537 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5215
538 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5216
539 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5217
540 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5218
541 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5219
542 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5220
543 | Mahisbathan int conn fdr | 33kV | I/C + Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5221
544 | Supreme+Modgul park fdr | 33kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 248
545 | Supreme+Modgul park fdr | 33kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 249
546 | Supreme+Modgul park fdr | 33kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 250
547 | Supreme+Modgul park fdr | 33kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 251
548 | Supreme+Modgul park fdr | 33kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 252
549 | Supreme+Modgul park fdr | 33kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 253
550 | Supreme+Modgul park fdr | 33kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 254
551 | Supreme+Modgul park fdr | 33kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 255
552 | Supreme+Modgul park fdr | 33kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 256
553 | Supreme+Modgul park fdr | 33kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 257
554 | Supreme+Modgul park fdr | 33kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 258
555 | Supreme+Modgul park fdr | 33kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 259
556 | Supreme+Modgul park fdr | 33kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13048
557 | Supreme+Modgul park fdr | 33kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13049
558 | Supreme+Modgul park fdr | 33kV | Outgoing | IED RESET | SPC |  |  | Soft | IED | 13050
559 | Supreme+Modgul park fdr | 33kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10012
560 | Supreme+Modgul park fdr | 33kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10012
561 | Supreme+Modgul park fdr | 33kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5222
562 | Supreme+Modgul park fdr | 33kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5223
563 | Supreme+Modgul park fdr | 33kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5224
564 | Supreme+Modgul park fdr | 33kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5225
565 | Supreme+Modgul park fdr | 33kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5226
566 | Supreme+Modgul park fdr | 33kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5227
567 | Supreme+Modgul park fdr | 33kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5228
568 | Supreme+Modgul park fdr | 33kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5229
569 | Supreme+Modgul park fdr | 33kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5230
570 | Supreme+Modgul park fdr | 33kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5231
571 | Supreme+Modgul park fdr | 33kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5232
572 | Supreme+Modgul park fdr | 33kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5233
573 | Supreme+Modgul park fdr | 33kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5234
574 | Supreme+Modgul park fdr | 33kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5235
575 | Supreme+Modgul park fdr | 33kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5236
576 | Supreme+Modgul park fdr | 33kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5237
577 | Supreme+Modgul park fdr | 33kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5238
578 | Supreme+Modgul park fdr | 33kV | Outgoing | Bus Voltage | AI |  |  | Soft | MFT | 5239
579 | Supreme+Modgul park fdr | 33kV | Outgoing | Bus Frequency | AI |  |  | Soft | MFT | 5240
580 | Tr4\Tr5 Inter connector | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 260
581 | Tr4\Tr5 Inter connector | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 261
582 | Tr4\Tr5 Inter connector | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 262
583 | Tr4\Tr5 Inter connector | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 263
584 | Tr4\Tr5 Inter connector | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 264
585 | Tr4\Tr5 Inter connector | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 265
586 | Tr4\Tr5 Inter connector | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 266
587 | Tr4\Tr5 Inter connector | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 267
588 | Tr4\Tr5 Inter connector | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 268
589 | Tr4\Tr5 Inter connector | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 269
590 | Tr4\Tr5 Inter connector | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 270
591 | Tr4\Tr5 Inter connector | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 271
592 | Tr4\Tr5 Inter connector | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 272
593 | Tr4\Tr5 Inter connector | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10013
594 | Tr4\Tr5 Inter connector | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10013
595 | Tr4\Tr5 Inter connector | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13051
596 | Tr4\Tr5 Inter connector | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13052
597 | Tr4\Tr5 Inter connector | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13053
598 | Tr4\Tr5 Inter connector | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5241
599 | Tr4\Tr5 Inter connector | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5242
600 | Tr4\Tr5 Inter connector | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5243
601 | Tr4\Tr5 Inter connector | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5244
602 | Tr4\Tr5 Inter connector | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5245
603 | Tr4\Tr5 Inter connector | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5246
604 | Tr4\Tr5 Inter connector | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5247
605 | Tr4\Tr5 Inter connector | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5248
606 | Tr4\Tr5 Inter connector | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5249
607 | Tr4\Tr5 Inter connector | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5250
608 | Tr4\Tr5 Inter connector | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5251
609 | Tr4\Tr5 Inter connector | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5252
610 | Tr4\Tr5 Inter connector | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5253
611 | Tr4\Tr5 Inter connector | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5254
612 | Tr4\Tr5 Inter connector | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5255
613 | Tr4\Tr5 Inter connector | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5256
614 | Tr4\Tr5 Inter connector | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5257
615 | 10 Pole+ IICB | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 273
616 | 10 Pole+ IICB | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 274
617 | 10 Pole+ IICB | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 275
618 | 10 Pole+ IICB | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 276
619 | 10 Pole+ IICB | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 277
620 | 10 Pole+ IICB | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 278
621 | 10 Pole+ IICB | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 279
622 | 10 Pole+ IICB | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 280
623 | 10 Pole+ IICB | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 281
624 | 10 Pole+ IICB | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 282
625 | 10 Pole+ IICB | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 283
626 | 10 Pole+ IICB | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 284
627 | 10 Pole+ IICB | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 285
628 | 10 Pole+ IICB | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 286
629 | 10 Pole+ IICB | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10014
630 | 10 Pole+ IICB | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10014
631 | 10 Pole+ IICB | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13054
632 | 10 Pole+ IICB | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13055
633 | 10 Pole+ IICB | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13056
634 | 10 Pole+ IICB | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5258
635 | 10 Pole+ IICB | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5259
636 | 10 Pole+ IICB | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5260
637 | 10 Pole+ IICB | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5261
638 | 10 Pole+ IICB | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5262
639 | 10 Pole+ IICB | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5263
640 | 10 Pole+ IICB | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5264
641 | 10 Pole+ IICB | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5265
642 | 10 Pole+ IICB | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5266
643 | 10 Pole+ IICB | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5267
644 | 10 Pole+ IICB | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5268
645 | 10 Pole+ IICB | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5269
646 | 10 Pole+ IICB | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5270
647 | 10 Pole+ IICB | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5271
648 | 10 Pole+ IICB | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5272
649 | 10 Pole+ IICB | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5273
650 | 10 Pole+ IICB | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5274
651 | Incoming-4 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 287
652 | Incoming-4 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 288
653 | Incoming-4 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 289
654 | Incoming-4 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 290
655 | Incoming-4 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 291
656 | Incoming-4 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 292
657 | Incoming-4 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 293
658 | Incoming-4 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 294
659 | Incoming-4 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 295
660 | Incoming-4 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 296
661 | Incoming-4 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 297
662 | Incoming-4 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 298
663 | Incoming-4 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 299
664 | Incoming-4 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10015
665 | Incoming-4 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10015
666 | Incoming-4 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13057
667 | Incoming-4 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13058
668 | Incoming-4 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13059
669 | Incoming-4 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5275
670 | Incoming-4 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5276
671 | Incoming-4 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5277
672 | Incoming-4 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5278
673 | Incoming-4 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5279
674 | Incoming-4 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5280
675 | Incoming-4 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5281
676 | Incoming-4 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5282
677 | Incoming-4 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5283
678 | Incoming-4 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5284
679 | Incoming-4 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5285
680 | Incoming-4 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5286
681 | Incoming-4 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5287
682 | Incoming-4 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5288
683 | Incoming-4 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5289
684 | Incoming-4 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5290
685 | Incoming-4 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5291
686 | ITT-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 300
687 | ITT-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 301
688 | ITT-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 302
689 | ITT-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 303
690 | ITT-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 304
691 | ITT-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 305
692 | ITT-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 306
693 | ITT-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 307
694 | ITT-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 308
695 | ITT-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 309
696 | ITT-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 310
697 | ITT-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 311
698 | ITT-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 312
699 | ITT-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 313
700 | ITT-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10016
701 | ITT-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10016
702 | ITT-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13060
703 | ITT-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13061
704 | ITT-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13062
705 | ITT-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5292
706 | ITT-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5293
707 | ITT-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5294
708 | ITT-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5295
709 | ITT-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5296
710 | ITT-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5297
711 | ITT-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5298
712 | ITT-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5299
713 | ITT-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5300
714 | ITT-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5301
715 | ITT-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5302
716 | ITT-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5303
717 | ITT-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5304
718 | ITT-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5305
719 | ITT-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5306
720 | ITT-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5307
721 | ITT-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5308
722 | TCS-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 314
723 | TCS-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 315
724 | TCS-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 316
725 | TCS-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 317
726 | TCS-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 318
727 | TCS-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 319
728 | TCS-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 320
729 | TCS-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 321
730 | TCS-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 322
731 | TCS-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 323
732 | TCS-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 324
733 | TCS-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 325
734 | TCS-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 326
735 | TCS-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 327
736 | TCS-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10017
737 | TCS-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10017
738 | TCS-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13063
739 | TCS-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13064
740 | TCS-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13065
741 | TCS-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5309
742 | TCS-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5310
743 | TCS-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5311
744 | TCS-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5312
745 | TCS-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5313
746 | TCS-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5314
747 | TCS-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5315
748 | TCS-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5316
749 | TCS-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5317
750 | TCS-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5318
751 | TCS-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5319
752 | TCS-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5320
753 | TCS-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5321
754 | TCS-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5322
755 | TCS-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5323
756 | TCS-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5324
757 | TCS-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5325
758 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 328
759 | Bus Coupler-4 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 329
760 | Bus Coupler-4 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 330
761 | Bus Coupler-4 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 331
762 | Bus Coupler-4 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 332
763 | Bus Coupler-4 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 333
764 | Bus Coupler-4 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 334
765 | Bus Coupler-4 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 335 |  |  |  | AC CMR to be used
766 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 336
767 | Bus Coupler-4 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 337
768 | Bus Coupler-4 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10018
769 | Bus Coupler-4 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10018
770 | SS-4 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 338
771 | SS-4 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 339
772 | SS-4 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 340
773 | SS-4 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 341
774 | SS-4 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 342
775 | SS-4 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 343
776 | SS-4 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 344
777 | SS-4 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 345
778 | SS-4 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 346
779 | SS-4 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 347
780 | SS-4 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 348
781 | SS-4 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 349
782 | SS-4 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 350
783 | SS-4 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 351
784 | SS-4 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10019
785 | SS-4 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10019
786 | SS-4 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13066
787 | SS-4 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13067
788 | SS-4 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13068
789 | SS-4 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5326
790 | SS-4 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5327
791 | SS-4 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5328
792 | SS-4 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5329
793 | SS-4 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5330
794 | SS-4 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5331
795 | SS-4 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5332
796 | SS-4 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5333
797 | SS-4 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5334
798 | SS-4 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5335
799 | SS-4 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5336
800 | SS-4 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5337
801 | SS-4 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5338
802 | SS-4 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5339
803 | SS-4 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5340
804 | SS-4 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5341
805 | SS-4 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5342
806 | H Guru | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 352
807 | H Guru | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 353
808 | H Guru | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 354
809 | H Guru | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 355
810 | H Guru | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 356
811 | H Guru | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 357
812 | H Guru | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 358
813 | H Guru | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 359
814 | H Guru | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 360
815 | H Guru | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 361
816 | H Guru | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 362
817 | H Guru | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 363
818 | H Guru | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 364
819 | H Guru | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 365
820 | H Guru | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10020
821 | H Guru | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10020
822 | H Guru | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13069
823 | H Guru | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13070
824 | H Guru | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13071
825 | H Guru | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5343
826 | H Guru | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5344
827 | H Guru | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5345
828 | H Guru | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5346
829 | H Guru | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5347
830 | H Guru | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5348
831 | H Guru | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5349
832 | H Guru | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5350
833 | H Guru | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5351
834 | H Guru | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5352
835 | H Guru | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5353
836 | H Guru | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5354
837 | H Guru | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5355
838 | H Guru | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5356
839 | H Guru | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5357
840 | H Guru | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5358
841 | H Guru | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5359
842 | CCAP | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 366
843 | CCAP | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 367
844 | CCAP | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 368
845 | CCAP | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 369
846 | CCAP | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 370
847 | CCAP | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 371
848 | CCAP | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 372
849 | CCAP | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 373
850 | CCAP | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 374
851 | CCAP | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 375
852 | CCAP | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 376
853 | CCAP | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 377
854 | CCAP | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 378
855 | CCAP | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 379
856 | CCAP | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10021
857 | CCAP | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10021
858 | CCAP | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13072
859 | CCAP | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13073
860 | CCAP | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13074
861 | CCAP | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5360
862 | CCAP | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5361
863 | CCAP | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5362
864 | CCAP | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5363
865 | CCAP | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5364
866 | CCAP | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5365
867 | CCAP | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5366
868 | CCAP | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5367
869 | CCAP | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5368
870 | CCAP | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5369
871 | CCAP | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5370
872 | CCAP | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5371
873 | CCAP | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5372
874 | CCAP | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5373
875 | CCAP | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5374
876 | CCAP | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5375
877 | CCAP | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5376
878 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 380
879 | Bus Coupler-3 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 381
880 | Bus Coupler-3 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 382
881 | Bus Coupler-3 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 383
882 | Bus Coupler-3 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 384
883 | Bus Coupler-3 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 385
884 | Bus Coupler-3 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 386
885 | Bus Coupler-3 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 387 |  |  |  | AC CMR to be used
886 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 388
887 | Bus Coupler-3 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 389
888 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10022
889 | Bus Coupler-3 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10022
890 | OH Sec V | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 390
891 | OH Sec V | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 391
892 | OH Sec V | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 392
893 | OH Sec V | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 393
894 | OH Sec V | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 394
895 | OH Sec V | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 395
896 | OH Sec V | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 396
897 | OH Sec V | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 397
898 | OH Sec V | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 398
899 | OH Sec V | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 399
900 | OH Sec V | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 400
901 | OH Sec V | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 401
902 | OH Sec V | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 402
903 | OH Sec V | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 403
904 | OH Sec V | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10023
905 | OH Sec V | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10023
906 | OH Sec V | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13075
907 | OH Sec V | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13076
908 | OH Sec V | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13077
909 | OH Sec V | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5377
910 | OH Sec V | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5378
911 | OH Sec V | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5379
912 | OH Sec V | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5380
913 | OH Sec V | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5381
914 | OH Sec V | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5382
915 | OH Sec V | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5383
916 | OH Sec V | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5384
917 | OH Sec V | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5385
918 | OH Sec V | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5386
919 | OH Sec V | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5387
920 | OH Sec V | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5388
921 | OH Sec V | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5389
922 | OH Sec V | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5390
923 | OH Sec V | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5391
924 | OH Sec V | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5392
925 | OH Sec V | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5393
926 | Mahisbathan fdr | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 404
927 | Mahisbathan fdr | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 405
928 | Mahisbathan fdr | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 406
929 | Mahisbathan fdr | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 407
930 | Mahisbathan fdr | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 408
931 | Mahisbathan fdr | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 409
932 | Mahisbathan fdr | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 410
933 | Mahisbathan fdr | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 411
934 | Mahisbathan fdr | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 412
935 | Mahisbathan fdr | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 413
936 | Mahisbathan fdr | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 414
937 | Mahisbathan fdr | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 415
938 | Mahisbathan fdr | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 416
939 | Mahisbathan fdr | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 417
940 | Mahisbathan fdr | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10024
941 | Mahisbathan fdr | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10024
942 | Mahisbathan fdr | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13078
943 | Mahisbathan fdr | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13079
944 | Mahisbathan fdr | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13080
945 | Mahisbathan fdr | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5394
946 | Mahisbathan fdr | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5395
947 | Mahisbathan fdr | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5396
948 | Mahisbathan fdr | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5397
949 | Mahisbathan fdr | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5398
950 | Mahisbathan fdr | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5399
951 | Mahisbathan fdr | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5400
952 | Mahisbathan fdr | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5401
953 | Mahisbathan fdr | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5402
954 | Mahisbathan fdr | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5403
955 | Mahisbathan fdr | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5404
956 | Mahisbathan fdr | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5405
957 | Mahisbathan fdr | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5406
958 | Mahisbathan fdr | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5407
959 | Mahisbathan fdr | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5408
960 | Mahisbathan fdr | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5409
961 | Mahisbathan fdr | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5410
962 | PTI | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 418
963 | PTI | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 419
964 | PTI | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 420
965 | PTI | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 421
966 | PTI | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 422
967 | PTI | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 423
968 | PTI | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 424
969 | PTI | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 425
970 | PTI | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 426
971 | PTI | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 427
972 | PTI | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 428
973 | PTI | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 429
974 | PTI | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 430
975 | PTI | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 431
976 | PTI | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10025
977 | PTI | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10025
978 | PTI | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13081
979 | PTI | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13082
980 | PTI | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13083
981 | PTI | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5411
982 | PTI | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5412
983 | PTI | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5413
984 | PTI | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5414
985 | PTI | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5415
986 | PTI | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5416
987 | PTI | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5417
988 | PTI | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5418
989 | PTI | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5419
990 | PTI | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5420
991 | PTI | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5421
992 | PTI | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5422
993 | PTI | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5423
994 | PTI | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5424
995 | PTI | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5425
996 | PTI | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5426
997 | PTI | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5427
998 | Incoming-3 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 432
999 | Incoming-3 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 433
1000 | Incoming-3 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 434
1001 | Incoming-3 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 435
1002 | Incoming-3 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 436
1003 | Incoming-3 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 437
1004 | Incoming-3 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 438
1005 | Incoming-3 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 439
1006 | Incoming-3 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 440
1007 | Incoming-3 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 441
1008 | Incoming-3 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 442
1009 | Incoming-3 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 443
1010 | Incoming-3 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 444
1011 | Incoming-3 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10026
1012 | Incoming-3 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10026
1013 | Incoming-3 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13084
1014 | Incoming-3 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13085
1015 | Incoming-3 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13086
1016 | Incoming-3 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5428
1017 | Incoming-3 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5429
1018 | Incoming-3 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5430
1019 | Incoming-3 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5431
1020 | Incoming-3 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5432
1021 | Incoming-3 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5433
1022 | Incoming-3 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5434
1023 | Incoming-3 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5435
1024 | Incoming-3 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5436
1025 | Incoming-3 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5437
1026 | Incoming-3 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5438
1027 | Incoming-3 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5439
1028 | Incoming-3 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5440
1029 | Incoming-3 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5441
1030 | Incoming-3 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5442
1031 | Incoming-3 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5443
1032 | Incoming-3 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5444
1033 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 445
1034 | Bus Coupler-2 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 446
1035 | Bus Coupler-2 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 447
1036 | Bus Coupler-2 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 448
1037 | Bus Coupler-2 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 449
1038 | Bus Coupler-2 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 450
1039 | Bus Coupler-2 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 451
1040 | Bus Coupler-2 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 452 |  |  |  | AC CMR to be used
1041 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 453
1042 | Bus Coupler-2 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 454
1043 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10027
1044 | Bus Coupler-2 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10027
1045 | NTH | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 455
1046 | NTH | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 456
1047 | NTH | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 457
1048 | NTH | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 458
1049 | NTH | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 459
1050 | NTH | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 460
1051 | NTH | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 461
1052 | NTH | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 462
1053 | NTH | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 463
1054 | NTH | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 464
1055 | NTH | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 465
1056 | NTH | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 466
1057 | NTH | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 467
1058 | NTH | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 468
1059 | NTH | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10028
1060 | NTH | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10028
1061 | NTH | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13087
1062 | NTH | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13088
1063 | NTH | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13089
1064 | NTH | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5445
1065 | NTH | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5446
1066 | NTH | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5447
1067 | NTH | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5448
1068 | NTH | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5449
1069 | NTH | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5450
1070 | NTH | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5451
1071 | NTH | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5452
1072 | NTH | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5453
1073 | NTH | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5454
1074 | NTH | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5455
1075 | NTH | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5456
1076 | NTH | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5457
1077 | NTH | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5458
1078 | NTH | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5459
1079 | NTH | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5460
1080 | NTH | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5461
1081 | DN-5\Magnacon | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 469
1082 | DN-5\Magnacon | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 470
1083 | DN-5\Magnacon | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 471
1084 | DN-5\Magnacon | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 472
1085 | DN-5\Magnacon | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 473
1086 | DN-5\Magnacon | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 474
1087 | DN-5\Magnacon | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 475
1088 | DN-5\Magnacon | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 476
1089 | DN-5\Magnacon | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 477
1090 | DN-5\Magnacon | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 478
1091 | DN-5\Magnacon | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 479
1092 | DN-5\Magnacon | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 480
1093 | DN-5\Magnacon | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 481
1094 | DN-5\Magnacon | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 482
1095 | DN-5\Magnacon | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10029
1096 | DN-5\Magnacon | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10029
1097 | DN-5\Magnacon | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13090
1098 | DN-5\Magnacon | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13091
1099 | DN-5\Magnacon | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13092
1100 | DN-5\Magnacon | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5462
1101 | DN-5\Magnacon | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5463
1102 | DN-5\Magnacon | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5464
1103 | DN-5\Magnacon | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5465
1104 | DN-5\Magnacon | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5466
1105 | DN-5\Magnacon | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5467
1106 | DN-5\Magnacon | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5468
1107 | DN-5\Magnacon | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5469
1108 | DN-5\Magnacon | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5470
1109 | DN-5\Magnacon | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5471
1110 | DN-5\Magnacon | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5472
1111 | DN-5\Magnacon | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5473
1112 | DN-5\Magnacon | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5474
1113 | DN-5\Magnacon | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5475
1114 | DN-5\Magnacon | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5476
1115 | DN-5\Magnacon | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5477
1116 | DN-5\Magnacon | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5478
1117 | SS-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 483
1118 | SS-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 484
1119 | SS-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 485
1120 | SS-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 486
1121 | SS-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 487
1122 | SS-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 488
1123 | SS-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 489
1124 | SS-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 490
1125 | SS-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 491
1126 | SS-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 492
1127 | SS-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 493
1128 | SS-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 494
1129 | SS-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 495
1130 | SS-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 496
1131 | SS-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10030
1132 | SS-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10030
1133 | SS-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13093
1134 | SS-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13094
1135 | SS-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13095
1136 | SS-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5479
1137 | SS-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5480
1138 | SS-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5481
1139 | SS-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5482
1140 | SS-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5483
1141 | SS-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5484
1142 | SS-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5485
1143 | SS-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5486
1144 | SS-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5487
1145 | SS-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5488
1146 | SS-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5489
1147 | SS-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5490
1148 | SS-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5491
1149 | SS-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5492
1150 | SS-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5493
1151 | SS-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5494
1152 | SS-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5495
1153 | Incoming-2 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 497
1154 | Incoming-2 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 498
1155 | Incoming-2 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 499
1156 | Incoming-2 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 500
1157 | Incoming-2 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 501
1158 | Incoming-2 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 502
1159 | Incoming-2 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 503
1160 | Incoming-2 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 504
1161 | Incoming-2 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 505
1162 | Incoming-2 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 506
1163 | Incoming-2 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 507
1164 | Incoming-2 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 508
1165 | Incoming-2 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 509
1166 | Incoming-2 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10031
1167 | Incoming-2 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10031
1168 | Incoming-2 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13096
1169 | Incoming-2 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13097
1170 | Incoming-2 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13098
1171 | Incoming-2 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5496
1172 | Incoming-2 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5497
1173 | Incoming-2 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5498
1174 | Incoming-2 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5499
1175 | Incoming-2 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5500
1176 | Incoming-2 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5501
1177 | Incoming-2 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5502
1178 | Incoming-2 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5503
1179 | Incoming-2 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5504
1180 | Incoming-2 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5505
1181 | Incoming-2 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5506
1182 | Incoming-2 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5507
1183 | Incoming-2 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5508
1184 | Incoming-2 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5509
1185 | Incoming-2 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5510
1186 | Incoming-2 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5511
1187 | Incoming-2 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5512
1188 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 510
1189 | Bus Coupler-1 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 511
1190 | Bus Coupler-1 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 512
1191 | Bus Coupler-1 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 513
1192 | Bus Coupler-1 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 514
1193 | Bus Coupler-1 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 515
1194 | Bus Coupler-1 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 516
1195 | Bus Coupler-1 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 517 |  |  |  | AC CMR to be used
1196 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 518
1197 | Bus Coupler-1 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 519
1198 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10032
1199 | Bus Coupler-1 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10032
1200 | Manikanchan fdr-1 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 520
1201 | Manikanchan fdr-1 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 521
1202 | Manikanchan fdr-1 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 522
1203 | Manikanchan fdr-1 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 523
1204 | Manikanchan fdr-1 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 524
1205 | Manikanchan fdr-1 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 525
1206 | Manikanchan fdr-1 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 526
1207 | Manikanchan fdr-1 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 527
1208 | Manikanchan fdr-1 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 528
1209 | Manikanchan fdr-1 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 529
1210 | Manikanchan fdr-1 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 530
1211 | Manikanchan fdr-1 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 531
1212 | Manikanchan fdr-1 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 532
1213 | Manikanchan fdr-1 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 533
1214 | Manikanchan fdr-1 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10033
1215 | Manikanchan fdr-1 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10033
1216 | Manikanchan fdr-1 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13099
1217 | Manikanchan fdr-1 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13100
1218 | Manikanchan fdr-1 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13101
1219 | Manikanchan fdr-1 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5513
1220 | Manikanchan fdr-1 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5514
1221 | Manikanchan fdr-1 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5515
1222 | Manikanchan fdr-1 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5516
1223 | Manikanchan fdr-1 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5517
1224 | Manikanchan fdr-1 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5518
1225 | Manikanchan fdr-1 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5519
1226 | Manikanchan fdr-1 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5520
1227 | Manikanchan fdr-1 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5521
1228 | Manikanchan fdr-1 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5522
1229 | Manikanchan fdr-1 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5523
1230 | Manikanchan fdr-1 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5524
1231 | Manikanchan fdr-1 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5525
1232 | Manikanchan fdr-1 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5526
1233 | Manikanchan fdr-1 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5527
1234 | Manikanchan fdr-1 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5528
1235 | Manikanchan fdr-1 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5529
1236 | Aaj kaal fdr | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 534
1237 | Aaj kaal fdr | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 535
1238 | Aaj kaal fdr | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 536
1239 | Aaj kaal fdr | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 537
1240 | Aaj kaal fdr | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 538
1241 | Aaj kaal fdr | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 539
1242 | Aaj kaal fdr | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 540
1243 | Aaj kaal fdr | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 541
1244 | Aaj kaal fdr | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 542
1245 | Aaj kaal fdr | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 543
1246 | Aaj kaal fdr | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 544
1247 | Aaj kaal fdr | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 545
1248 | Aaj kaal fdr | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 546
1249 | Aaj kaal fdr | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 547
1250 | Aaj kaal fdr | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10034
1251 | Aaj kaal fdr | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10034
1252 | Aaj kaal fdr | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13102
1253 | Aaj kaal fdr | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13103
1254 | Aaj kaal fdr | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13104
1255 | Aaj kaal fdr | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5530
1256 | Aaj kaal fdr | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5531
1257 | Aaj kaal fdr | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5532
1258 | Aaj kaal fdr | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5533
1259 | Aaj kaal fdr | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5534
1260 | Aaj kaal fdr | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5535
1261 | Aaj kaal fdr | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5536
1262 | Aaj kaal fdr | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5537
1263 | Aaj kaal fdr | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5538
1264 | Aaj kaal fdr | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5539
1265 | Aaj kaal fdr | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5540
1266 | Aaj kaal fdr | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5541
1267 | Aaj kaal fdr | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5542
1268 | Aaj kaal fdr | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5543
1269 | Aaj kaal fdr | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5544
1270 | Aaj kaal fdr | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5545
1271 | Aaj kaal fdr | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5546
1272 | Saltee tech DN-18 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 548
1273 | Saltee tech DN-18 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 549
1274 | Saltee tech DN-18 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 550
1275 | Saltee tech DN-18 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 551
1276 | Saltee tech DN-18 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 552
1277 | Saltee tech DN-18 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 553
1278 | Saltee tech DN-18 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 554
1279 | Saltee tech DN-18 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 555
1280 | Saltee tech DN-18 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 556
1281 | Saltee tech DN-18 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 557
1282 | Saltee tech DN-18 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 558
1283 | Saltee tech DN-18 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 559
1284 | Saltee tech DN-18 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 560
1285 | Saltee tech DN-18 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 561
1286 | Saltee tech DN-18 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10035
1287 | Saltee tech DN-18 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10035
1288 | Saltee tech DN-18 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13105
1289 | Saltee tech DN-18 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13106
1290 | Saltee tech DN-18 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13107
1291 | Saltee tech DN-18 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5547
1292 | Saltee tech DN-18 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5548
1293 | Saltee tech DN-18 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5549
1294 | Saltee tech DN-18 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5550
1295 | Saltee tech DN-18 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5551
1296 | Saltee tech DN-18 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5552
1297 | Saltee tech DN-18 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5553
1298 | Saltee tech DN-18 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5554
1299 | Saltee tech DN-18 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5555
1300 | Saltee tech DN-18 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5556
1301 | Saltee tech DN-18 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5557
1302 | Saltee tech DN-18 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5558
1303 | Saltee tech DN-18 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5559
1304 | Saltee tech DN-18 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5560
1305 | Saltee tech DN-18 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5561
1306 | Saltee tech DN-18 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5562
1307 | Saltee tech DN-18 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5563
1308 | M-V Over head fdr | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 562
1309 | M-V Over head fdr | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 563
1310 | M-V Over head fdr | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 564
1311 | M-V Over head fdr | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 565
1312 | M-V Over head fdr | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 566
1313 | M-V Over head fdr | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 567
1314 | M-V Over head fdr | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 568
1315 | M-V Over head fdr | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 569
1316 | M-V Over head fdr | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 570
1317 | M-V Over head fdr | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 571
1318 | M-V Over head fdr | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 572
1319 | M-V Over head fdr | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 573
1320 | M-V Over head fdr | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 574
1321 | M-V Over head fdr | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 575
1322 | M-V Over head fdr | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10036
1323 | M-V Over head fdr | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10036
1324 | M-V Over head fdr | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13108
1325 | M-V Over head fdr | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13109
1326 | M-V Over head fdr | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13110
1327 | M-V Over head fdr | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5564
1328 | M-V Over head fdr | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5565
1329 | M-V Over head fdr | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5566
1330 | M-V Over head fdr | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5567
1331 | M-V Over head fdr | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5568
1332 | M-V Over head fdr | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5569
1333 | M-V Over head fdr | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5570
1334 | M-V Over head fdr | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5571
1335 | M-V Over head fdr | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5572
1336 | M-V Over head fdr | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5573
1337 | M-V Over head fdr | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5574
1338 | M-V Over head fdr | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5575
1339 | M-V Over head fdr | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5576
1340 | M-V Over head fdr | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5577
1341 | M-V Over head fdr | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5578
1342 | M-V Over head fdr | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5579
1343 | M-V Over head fdr | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5580
1344 | Incoming-1 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 576
1345 | Incoming-1 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 577
1346 | Incoming-1 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 578
1347 | Incoming-1 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 579
1348 | Incoming-1 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 580
1349 | Incoming-1 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 581
1350 | Incoming-1 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 582
1351 | Incoming-1 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 583
1352 | Incoming-1 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 584
1353 | Incoming-1 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 585
1354 | Incoming-1 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 586
1355 | Incoming-1 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 587
1356 | Incoming-1 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 588
1357 | Incoming-1 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10037
1358 | Incoming-1 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10037
1359 | Incoming-1 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13111
1360 | Incoming-1 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13112
1361 | Incoming-1 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13113
1362 | Incoming-1 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5581
1363 | Incoming-1 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5582
1364 | Incoming-1 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5583
1365 | Incoming-1 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5584
1366 | Incoming-1 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5585
1367 | Incoming-1 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5586
1368 | Incoming-1 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5587
1369 | Incoming-1 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5588
1370 | Incoming-1 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5589
1371 | Incoming-1 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5590
1372 | Incoming-1 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5591
1373 | Incoming-1 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5592
1374 | Incoming-1 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5593
1375 | Incoming-1 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5594
1376 | Incoming-1 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5595
1377 | Incoming-1 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5596
1378 | Incoming-1 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5597
1379 | Tr5\Tr4 Inter connector | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 589
1380 | Tr5\Tr4 Inter connector | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 590
1381 | Tr5\Tr4 Inter connector | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 591
1382 | Tr5\Tr4 Inter connector | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 592
1383 | Tr5\Tr4 Inter connector | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 593
1384 | Tr5\Tr4 Inter connector | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 594
1385 | Tr5\Tr4 Inter connector | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 595
1386 | Tr5\Tr4 Inter connector | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 596
1387 | Tr5\Tr4 Inter connector | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 597
1388 | Tr5\Tr4 Inter connector | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 598
1389 | Tr5\Tr4 Inter connector | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 599
1390 | Tr5\Tr4 Inter connector | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 600
1391 | Tr5\Tr4 Inter connector | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 601
1392 | Tr5\Tr4 Inter connector | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10038
1393 | Tr5\Tr4 Inter connector | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10038
1394 | Tr5\Tr4 Inter connector | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13114
1395 | Tr5\Tr4 Inter connector | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13115
1396 | Tr5\Tr4 Inter connector | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13116
1397 | Tr5\Tr4 Inter connector | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5598
1398 | Tr5\Tr4 Inter connector | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5599
1399 | Tr5\Tr4 Inter connector | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5600
1400 | Tr5\Tr4 Inter connector | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5601
1401 | Tr5\Tr4 Inter connector | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5602
1402 | Tr5\Tr4 Inter connector | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5603
1403 | Tr5\Tr4 Inter connector | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5604
1404 | Tr5\Tr4 Inter connector | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5605
1405 | Tr5\Tr4 Inter connector | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5606
1406 | Tr5\Tr4 Inter connector | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5607
1407 | Tr5\Tr4 Inter connector | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5608
1408 | Tr5\Tr4 Inter connector | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5609
1409 | Tr5\Tr4 Inter connector | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5610
1410 | Tr5\Tr4 Inter connector | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5611
1411 | Tr5\Tr4 Inter connector | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5612
1412 | Tr5\Tr4 Inter connector | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5613
1413 | Tr5\Tr4 Inter connector | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5614
1414 | Simoco | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 602
1415 | Simoco | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 603
1416 | Simoco | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 604
1417 | Simoco | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 605
1418 | Simoco | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 606
1419 | Simoco | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 607
1420 | Simoco | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 608
1421 | Simoco | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 609
1422 | Simoco | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 610
1423 | Simoco | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 611
1424 | Simoco | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 612
1425 | Simoco | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 613
1426 | Simoco | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 614
1427 | Simoco | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 615
1428 | Simoco | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10039
1429 | Simoco | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10039
1430 | Simoco | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13117
1431 | Simoco | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13118
1432 | Simoco | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13119
1433 | Simoco | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5615
1434 | Simoco | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5616
1435 | Simoco | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5617
1436 | Simoco | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5618
1437 | Simoco | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5619
1438 | Simoco | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5620
1439 | Simoco | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5621
1440 | Simoco | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5622
1441 | Simoco | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5623
1442 | Simoco | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5624
1443 | Simoco | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5625
1444 | Simoco | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5626
1445 | Simoco | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5627
1446 | Simoco | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5628
1447 | Simoco | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5629
1448 | Simoco | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5630
1449 | Simoco | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5631
1450 | Manikanchan fdr-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 616
1451 | Manikanchan fdr-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 617
1452 | Manikanchan fdr-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 618
1453 | Manikanchan fdr-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 619
1454 | Manikanchan fdr-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 620
1455 | Manikanchan fdr-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 621
1456 | Manikanchan fdr-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 622
1457 | Manikanchan fdr-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 623
1458 | Manikanchan fdr-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 624
1459 | Manikanchan fdr-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 625
1460 | Manikanchan fdr-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 626
1461 | Manikanchan fdr-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 627
1462 | Manikanchan fdr-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 628
1463 | Manikanchan fdr-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 629
1464 | Manikanchan fdr-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10040
1465 | Manikanchan fdr-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10040
1466 | Manikanchan fdr-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13120
1467 | Manikanchan fdr-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13121
1468 | Manikanchan fdr-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13122
1469 | Manikanchan fdr-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5632
1470 | Manikanchan fdr-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5633
1471 | Manikanchan fdr-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5634
1472 | Manikanchan fdr-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5635
1473 | Manikanchan fdr-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5636
1474 | Manikanchan fdr-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5637
1475 | Manikanchan fdr-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5638
1476 | Manikanchan fdr-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5639
1477 | Manikanchan fdr-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5640
1478 | Manikanchan fdr-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5641
1479 | Manikanchan fdr-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5642
1480 | Manikanchan fdr-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5643
1481 | Manikanchan fdr-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5644
1482 | Manikanchan fdr-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5645
1483 | Manikanchan fdr-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5646
1484 | Manikanchan fdr-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5647
1485 | Manikanchan fdr-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5648
1486 | Bus Coupler-5 | 11kV | Bus coupler | Circuit Breaker Close | SPI |  |  | Hard | CMR | 630
1487 | Bus Coupler-5 | 11kV | Bus coupler | Circuit Breaker Open | SPI |  |  | Hard | CMR | 631
1488 | Bus Coupler-5 | 11kV | Bus coupler | CB Trip Ckt Healthy | SPI |  |  | Hard | CMR | 632
1489 | Bus Coupler-5 | 11kV | Bus coupler | Spring Charged | SPI |  |  | Hard | CMR | 633
1490 | Bus Coupler-5 | 11kV | Bus coupler | Test Position | SPI |  |  | Hard | CMR | 634
1491 | Bus Coupler-5 | 11kV | Bus coupler | Service Position | SPI |  |  | Hard | CMR | 635
1492 | Bus Coupler-5 | 11kV | Bus coupler | DC Fail | SPI |  |  | Hard | CMR | 636
1493 | Bus Coupler-5 | 11kV | Bus coupler | AC Fail | SPI |  |  | Hard | CMR | 637 |  |  |  | AC CMR to be used
1494 | Bus Coupler-5 | 11kV | Bus coupler | C/R Panel Local Position | SPI |  |  | Hard | CMR | 638
1495 | Bus Coupler-5 | 11kV | Bus coupler | C/R Panel Remote Position | SPI |  |  | Hard | CMR | 639
1496 | Bus Coupler-5 | 11kV | Bus coupler | Circuit breaker Close Command | DPC |  |  | Hard | HDR | 10041
1497 | Bus Coupler-5 | 11kV | Bus coupler | Circuit breaker Open Command | DPC |  |  | Hard | HDR | 10041
1498 | Cognizant | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 640
1499 | Cognizant | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 641
1500 | Cognizant | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 642
1501 | Cognizant | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 643
1502 | Cognizant | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 644
1503 | Cognizant | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 645
1504 | Cognizant | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 646
1505 | Cognizant | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 647
1506 | Cognizant | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 648
1507 | Cognizant | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 649
1508 | Cognizant | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 650
1509 | Cognizant | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 651
1510 | Cognizant | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 652
1511 | Cognizant | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 653
1512 | Cognizant | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10042
1513 | Cognizant | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10042
1514 | Cognizant | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13123
1515 | Cognizant | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13124
1516 | Cognizant | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13125
1517 | Cognizant | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5649
1518 | Cognizant | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5650
1519 | Cognizant | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5651
1520 | Cognizant | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5652
1521 | Cognizant | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5653
1522 | Cognizant | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5654
1523 | Cognizant | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5655
1524 | Cognizant | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5656
1525 | Cognizant | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5657
1526 | Cognizant | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5658
1527 | Cognizant | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5659
1528 | Cognizant | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5660
1529 | Cognizant | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5661
1530 | Cognizant | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5662
1531 | Cognizant | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5663
1532 | Cognizant | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5664
1533 | Cognizant | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5665
1534 | STP-2 | 11kV | Outgoing | Circuit Breaker Close | SPI |  |  | Soft | IED | 654
1535 | STP-2 | 11kV | Outgoing | Circuit Breaker Open | SPI |  |  | Soft | IED | 655
1536 | STP-2 | 11kV | Outgoing | Auto Trip | SPI |  |  | Soft | IED | 656
1537 | STP-2 | 11kV | Outgoing | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 657
1538 | STP-2 | 11kV | Outgoing | Spring Charged | SPI |  |  | Soft | IED | 658
1539 | STP-2 | 11kV | Outgoing | Test Position | SPI |  |  | Hard | CMR | 659
1540 | STP-2 | 11kV | Outgoing | Service Position | SPI |  |  | Hard | CMR | 660
1541 | STP-2 | 11kV | Outgoing | Earth Fault Operated | SPI |  |  | Soft | IED | 661
1542 | STP-2 | 11kV | Outgoing | Broken conductor optd | SPI |  |  | Soft | IED | 662
1543 | STP-2 | 11kV | Outgoing | Over Current Operated | SPI |  |  | Soft | IED | 663
1544 | STP-2 | 11kV | Outgoing | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 664
1545 | STP-2 | 11kV | Outgoing | C/R Panel Local Position | SPI |  |  | Hard | CMR | 665
1546 | STP-2 | 11kV | Outgoing | C/R Panel Remote Position | SPI |  |  | Soft | IED | 666
1547 | STP-2 | 11kV | Outgoing | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 667
1548 | STP-2 | 11kV | Outgoing | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10043
1549 | STP-2 | 11kV | Outgoing | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10043
1550 | STP-2 | 11kV | Outgoing | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13126
1551 | STP-2 | 11kV | Outgoing | Annunciator reset | SPC |  |  | Hard | HDR | 13127
1552 | STP-2 | 11kV | Outgoing | IED Reset | SPC |  |  | Soft | IED | 13128
1553 | STP-2 | 11kV | Outgoing | Voltage RY | AI |  | 0-110V | Soft | MFT | 5666
1554 | STP-2 | 11kV | Outgoing | Voltage YB | AI |  | 0-110V | Soft | MFT | 5667
1555 | STP-2 | 11kV | Outgoing | Voltage BR | AI |  | 0-110V | Soft | MFT | 5668
1556 | STP-2 | 11kV | Outgoing | Current R Phase | AI |  | 1/5A | Soft | MFT | 5669
1557 | STP-2 | 11kV | Outgoing | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5670
1558 | STP-2 | 11kV | Outgoing | Current B Phase | AI |  | 1/5A | Soft | MFT | 5671
1559 | STP-2 | 11kV | Outgoing | Active Power | AI |  |  | Soft | MFT | 5672
1560 | STP-2 | 11kV | Outgoing | Reactive Power | AI |  |  | Soft | MFT | 5673
1561 | STP-2 | 11kV | Outgoing | Power Factor | AI |  |  | Soft | MFT | 5674
1562 | STP-2 | 11kV | Outgoing | Phase Angle R | AI |  |  | Soft | MFT | 5675
1563 | STP-2 | 11kV | Outgoing | Phase Angle Y | AI |  |  | Soft | MFT | 5676
1564 | STP-2 | 11kV | Outgoing | Phase Angle B | AI |  |  | Soft | MFT | 5677
1565 | STP-2 | 11kV | Outgoing | Active Energy Import | AI |  |  | Soft | MFT | 5678
1566 | STP-2 | 11kV | Outgoing | Active Energy Export | AI |  |  | Soft | MFT | 5679
1567 | STP-2 | 11kV | Outgoing | Reactive Energy Import | AI |  |  | Soft | MFT | 5680
1568 | STP-2 | 11kV | Outgoing | Reactive Energy Export | AI |  |  | Soft | MFT | 5681
1569 | STP-2 | 11kV | Outgoing | Unbalance Current | AI |  |  | Soft | MFT | 5682
1570 | incoming-5 | 11kV | Incomer | Circuit Breaker Close | SPI |  |  | Soft | IED | 668
1571 | incoming-5 | 11kV | Incomer | Circuit Breaker Open | SPI |  |  | Soft | IED | 669
1572 | incoming-5 | 11kV | Incomer | Auto Trip | SPI |  |  | Soft | IED | 670
1573 | incoming-5 | 11kV | Incomer | CB Trip Ckt Healthy | SPI |  |  | Soft | IED | 671
1574 | incoming-5 | 11kV | Incomer | Spring Charged | SPI |  |  | Soft | IED | 672
1575 | incoming-5 | 11kV | Incomer | Test Position | SPI |  |  | Hard | CMR | 673
1576 | incoming-5 | 11kV | Incomer | Service Position | SPI |  |  | Hard | CMR | 674
1577 | incoming-5 | 11kV | Incomer | Earth Fault Operated | SPI |  |  | Soft | IED | 675
1578 | incoming-5 | 11kV | Incomer | Over Current Operated | SPI |  |  | Soft | IED | 676
1579 | incoming-5 | 11kV | Incomer | Master Trip Relay Optd(MTR) | SPI |  |  | Soft | IED | 677
1580 | incoming-5 | 11kV | Incomer | C/R Panel Local Position | SPI |  |  | Hard | CMR | 678
1581 | incoming-5 | 11kV | Incomer | C/R Panel Remote Position | SPI |  |  | Soft | IED | 679
1582 | incoming-5 | 11kV | Incomer | Internal Relay Failure(IRF) of IED | SPI |  |  | Hard | CMR | 680
1583 | incoming-5 | 11kV | Incomer | Circuit breaker Close Command | DPC |  |  | Soft | IED | 10044
1584 | incoming-5 | 11kV | Incomer | Circuit breaker Open Command | DPC |  |  | Soft | IED | 10044
1585 | incoming-5 | 11kV | Incomer | Master Trip Relay Reset (MTR)+Annunciation accept | SPC |  |  | Hard | HDR | 13129
1586 | incoming-5 | 11kV | Incomer | Annunciator reset | SPC |  |  | Hard | HDR | 13130
1587 | incoming-5 | 11kV | Incomer | IED Reset | SPC |  |  | Soft | IED | 13131
1588 | incoming-5 | 11kV | Incomer | Voltage RY | AI |  | 0-110V | Soft | MFT | 5683
1589 | incoming-5 | 11kV | Incomer | Voltage YB | AI |  | 0-110V | Soft | MFT | 5684
1590 | incoming-5 | 11kV | Incomer | Voltage BR | AI |  | 0-110V | Soft | MFT | 5685
1591 | incoming-5 | 11kV | Incomer | Current R Phase | AI |  | 1/5A | Soft | MFT | 5686
1592 | incoming-5 | 11kV | Incomer | Current Y Phase | AI |  | 1/5A | Soft | MFT | 5687
1593 | incoming-5 | 11kV | Incomer | Current B Phase | AI |  | 1/5A | Soft | MFT | 5688
1594 | incoming-5 | 11kV | Incomer | Active Power | AI |  |  | Soft | MFT | 5689
1595 | incoming-5 | 11kV | Incomer | Reactive Power | AI |  |  | Soft | MFT | 5690
1596 | incoming-5 | 11kV | Incomer | Power Factor | AI |  |  | Soft | MFT | 5691
1597 | incoming-5 | 11kV | Incomer | Phase Angle R | AI |  |  | Soft | MFT | 5692
1598 | incoming-5 | 11kV | Incomer | Phase Angle Y | AI |  |  | Soft | MFT | 5693
1599 | incoming-5 | 11kV | Incomer | Phase Angle B | AI |  |  | Soft | MFT | 5694
1600 | incoming-5 | 11kV | Incomer | Active Energy Import | AI |  |  | Soft | MFT | 5695
1601 | incoming-5 | 11kV | Incomer | Active Energy Export | AI |  |  | Soft | MFT | 5696
1602 | incoming-5 | 11kV | Incomer | Reactive Energy Import | AI |  |  | Soft | MFT | 5697
1603 | incoming-5 | 11kV | Incomer | Reactive Energy Export | AI |  |  | Soft | MFT | 5698
1604 | incoming-5 | 11kV | Incomer | Unbalance Current | AI |  |  | Soft | MFT | 5699
1605 | ACDB | 0.415 KV | ACDB | Phase Voltage RN | AI |  |  | Soft | MFT | 5700
1606 | ACDB | 0.415 KV | ACDB | Phase Voltage YN | AI |  |  | Soft | MFT | 5701
1607 | ACDB | 0.415 KV | ACDB | Phase Voltage BN | AI |  |  | Soft | MFT | 5702
1608 | ACDB | 0.415 KV | ACDB | Current R Phase | AI |  |  | Soft | MFT | 5703
1609 | ACDB | 0.415 KV | ACDB | Current Y Phase | AI |  |  | Soft | MFT | 5704
1610 | ACDB | 0.415 KV | ACDB | Current B Phase | AI |  |  | Soft | MFT | 5705
1611 | ACDB | 0.415 KV | ACDB | Unbalance Current | AI |  |  | Soft | MFT | 5706